## Audit_Teams_Follow_Up
Team No. | Rig No. | Job Type | Well Name | Field | Starting Date | Job Days | Expected Rig

## Drops_Teams_Follow_Up
Team No. | Rig No. | Campaign No. | Rig_Last Visit | Mast Availability | Non Availability Reasons | Well Name | Field | Starting_Date | Job_Days
Team_1 | EDC-48 | 5th Campaign | 2023-08-29 | yes | No Reason | LITHIUM-1X | BERENICE | 2023-12-01 | 3

## All_Critical_Points
Rig_No. | No. | Location | Description | Priority | Ref. | Final_ Status | Phase | Rig Type
EDC-1 | No Critical | No Critical | No Critical | No Critical | No Critical | No Critical | No Critical | DRLG
EDC-9 | 4.5.21 | Intermediate Tank | Purge system on intermediate tank plug panel and mixing area plug panel not existed at all ( Purging is a method of installing electrical equipment in a classified location without using explosionproof enclosures) | Critical | API RP 14FZ 3.2.105/4.4.2/4.3.5 | In progress | FCS-2 | DRLG
EDC-9 | 5.10.43 | #### | Kitchen ventilation hood shows excessive grease from outside duct which presenting a serious fire hazard that require an immediate cleaning and to be directed for a monthly cleaning schedule. | Critical | API RP 54, NFPA 30, OSHA 1910.106 | Open | RA-2 | DRLG
EDC-9 | 5.7.7 | ### | CSB missing locking device operates when the lifting handle is in neutral. | Critical | IADC HSE Guidelines Ref 3.25 E | Open | FCS-1 | DRLG
EDC-11 | 1.7.33 | Rotary Hose | Rotary Hose (high pressure hose 5K psi) damaged in outer rubber shield, the metal shield expossed and corroded, in need to be replaced as per API STD clear mention. Moisture will enter into the reinforcement materials, and there are no existing means available to remove it. As a result, corrosion will occur to the reinforcement materials, which over time, will progress to the point where the strength of the reinforcing materials will be reduced, and the pressure integrity and useful life of the hose will be compromised. | Critical | API RP 7L_AD2 SEC. A6 | In progress | FCS-2 | DRLG
EDC-11 | 3.3.8 | Rotary Hose | Choke line coflexip hose, found completely damaged in external shield (coflex) which requires being replaced with certified one. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | DRLG
EDC-11 | 5.5.37 | Make-up & Break-out Cathead | Make-up & Break-out cathead wire rope sling showed fatigue failure ( Broken wires more than 6ea in different strands, birdcage and crushed ) which is meets for rejection criteria and highly require to remove from service to avoid sever injuries may occur in case the wire rope mechanical failure. | Critical | LOLER 1998 Regulations, API RP 9B, BS EN 13414, BS EN 10204 grade 1960, BS 1290 | In progress | RA-2 | DRLG
EDC-11 | 5.4.98 | Derrick | rig derrick ladder,Lad safe system turnbuckle not attached, lad system sleeve not at place | Critical | API RP 54 3.1.58 ASSE Z359.1, The Fall Protection Code | Open | RA-2 | DRLG
EDC-11 | 5.2.9 | Escape Device | The Derrick man's Escape Device (Geronimo) already rigged up at the derrick but the monkey board not provided with gate in the work platform’s guard railing for safe and effective exiting also to avoid CLIMB OVER ANYTHING TO GAIN ACCESS TO THE GERONIMO UNIT , which is recommended to provide the derrick man's platform with safe exit gate for best insure safe mounting and this would best insure safe mounting and effective exiting from the work area from the work area. | critical | OEM, API RP 54 6.12, IADC HSE Guidelines 3.15 | Open | FCS-2 | DRLG
EDC-12 | 5.7.20 | 0 | Improper anchoring for the fall arrest at the crown section due to it anchored at the crown section handrails which is should provide the mast with independent pad eye for anchorage point and must be capable of supporting at least 5000 pounds (2268 kilos)per employee also FYI most standard guardrail systems are not adequate anchorage points because they are not built to withstand the Impact forces generated by a fall. (Correction, found the fall arrest anchored at pad eye and this pad eye welded on piece of metal sheet welded on the crown section handrail and still there is no load test certifect submitted, also FYI most standard guardrail systems are not adequate anchorage points because they are not built to withstand the Impact forces generated by a fall). | Critical | IADC HSE Guidelines 20.3 C | open | FCS-3 | WO
EDC-17 | 4.11.32 | Elect/Mech Workshop | ELCB (Earth Leakage Circuit Breaker) installed in Elect / Mech Workshop Panel fail to trip manually ,also Fail to trip using RCD tester Need to be replaced Immediately. | Critical | IADC HSE Guidelines API RP 52, API RP 54, API RP 14FZ 9.4.2 | Open | RA-3 | DRLG
EDC-17 | 4.12.56 | Engine # 2 | Engine# 2 starter Motor is removed from the engine and set on engine Battery and very close to battery terminals , high risk to cause short circuit on the batteries terminals which lead to explosion lead to fire , need to carefully disconnect all wiring from the starter and remove the starter away from the batteries immediatly and also need to install rubber protection cover for the Battery terminal. | Critical | IADC HSE Guide Line , API RP 54 , NFPA , OEM/PMS | Open | RA-3 | DRLG
EDC-17 | 5.5.127 | 0 | Excessive amount of contaminated liquids with oil and diesel obstructed below engines #4, 2 and 1 due to the very bad condition of engines, that's may assist in the composition of the fire triangle and direct environmental impact, which needs to investigate for the main reason of spill, contamination to analyzing the hazard and to implementing an proactive monitoring plan as temporary solution for proper controlling of risk also to remove all this substances and keep the area in dry condition periodically to avoid HIPO of fire source and environmental impact. | critical | API RP 54, IADC HSE Guidelines | Open | RA-3 | DRLG
EDC-17 | 5.7.50 | 0 | During the deep inspection carried out on forklift find the rear left tire and spare tire totally worn out contained a excessive cuts in lips side(Internal layer was appeared) also the tire lips it is cleared, require to replace it to avoid the cut extended internally and in this time explosions may occur. Forklift (S/N: 6309167) | critical | IADC HSE Reference Guide chapter 9, OEM | Open | RA-3 | DRLG
EDC-17 | 5.7.51 | 0 | Multiple fail finding at the monkey board auxiliary escape system as following: A- Device far away from monkey board platform this makes it difficult to allow the user to mount the unit. B- No gate in the work platform guard railing for safe and effective exiting. Recommend proper rigging up for device, make the device reachable for user, provide the platform with gate for effective and safe exiting. | critical | OEM, API RP 54 6.12, IADC HSE Guidelines 3.15 | Open | RA-3 | DRLG
EDC-17 | 5.9.37 | 0 | Kitchen ventilation hood shows excessive grease from inside hood, outside duct and filters presenting a serious fire hazard which require an immediate cleaning and to be directed for a monthly cleaning schedule or where necessary | Critical | API RP 54 7.1, NFPA 30 | Open | FCS-2 | DRLG
EDC-17 | 5.10.18 | 0 | Automated External Defibrillator (AED) device is malfunction, require for replacing ASAP as it a life saving equipment and emergency medical equipment. Device S.N (73943004281). | Critical | API RP 54, IADC HSE Guidelines, OEM, WHO | Open | RA-3 | DRLG
EDC-31 | No Critical | No Critical | No Critical | No Critical | No Critical | No Critical | No Critical | PU
EDC-32 | 1.2.12 | Power Tong | Power tong rotating head not equipped with the safety door, operational lock-out device prevents tong from operation while door open. | Critical | OEM, API RP 54 (9), IADC HSE guide lines | Open | FCS-2 | PU
EDC-32 | 4.1.3 | Water tank | Watertreatment UV filter & chlorin down | CRITICAl | OEM/EDC Catring &Hajeen manual | OPEN | FCS-2 | PU
EDC-32 | 4.4.6 | RCD. | Fly camp offices RCD "Residual current Devise" & ELC earth leakage circuit not activted neutral phase not available in caravans maybe should to replace transformer to star connection, | CRITICAl | IADC HSE Guidelines API RP 52, API RP 54, API RP 14FZ 9.4.2 | OPEN | FCS-2 | PU
EDC-32 | 5.2.2 | 0 | There is no H2S fixed gas detector system available and required to be provided | critical | API RP 49 ,EDC safety manual,API RP 54, IADC HSE Guidelines | open | FCS-2 | PU
EDC-32 | 5.5.37 | Rig Floor | Lifting person by air winch not accepted very risky must be use man-riding machine .(safety instruction) | Critical | IADC HSE GUIDELINES and EDC safety manual | Open | FCS-1 | PU
EDC-42 | 1.4.44 | Set back area | Set back area wood found worn out and in poor condition require to be changed. | Critical | API RP 4F, API RP 4G | Open | FCS-2 | DRLG
EDC-42 | 2.3.61 | MP No.1 | Mud Pump (high pressure hose Vibrator Hose) between H.P surface line and stand pipe damaged in outer rubber shield and the metal shield corroded, in need to be replaced as per API STD clear mention. Moisture will enter into the reinforcement materials, and there are no existing means available to remove it. As a result, corrosion will occur to the reinforcement materials, which over time, will progress to the point where the strength of the reinforcing materials will be reduced, and the pressure integrity and useful life of the hose will be compromised. | Critical | API RP 7L_AD2 SEC. A6 | In progress | FCS-3 | DRLG
EDC-42 | 3.1.35 | BOP Control Hoses | Two BOP control system lines damaged in outer shield and there damaged in metal shield, all BOP control line has to be fire resistance and manufacture according API 16 D in need to be replaced. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | In progress | FCS-3 | DRLG
EDC-42 | 4.4.26 | Mud Pumps Control | MPs hand throttle controller has modified and installed in a homemade metal box the doesn't meet any standard classification, (item of electrical equipment must be tested or approved in order to comply with IEC 79 series publications, that item must be-(a) Listed or certified by an independent laboratory as approved for use in the hazardous locations in which it is installed; or (b)Purged and pressurized equipment that meets NFF’A No. 496or IEC 79-2). | Critical | API RP 14FZ, API RP 54,API RP 14F 4.3, 2.1, 111.105, NEMA tables, IADC HSE Guide line | Open | FCS-2 | DRLG
EDC-42 | 4.6.30 | Diesel Tank | Fuel Purifier AC motor is not Explosion Proof type need to be replaced by EX type motor. | Critical | API RP 505 8.2.1.3.1 , NFPA 30 ,IEC 60079-10 | Open | FCS-3 | DRLG
EDC-42 | 5.9.22 | ## | Only one PAD SET FOR AED (automated external defibrillator) used for CPR in the clinic found expired from 17-4-2023, new valid sets need to be provided ASAP | Critical | WHO, API RP 54, IADC HSE Guidelines | open | FCS-3 | DRLG
EDC-48 | 4.4.49 | Fuel Purifier | Fuel Purifier AC motor is not Explosion Proof type need to be replaced by EX type motor. | Critical | API RP 500 8.2.1.4 , API RP 14FZ , IADC HSE Guide Lines , IEC 60079 | In progress | RA-3 | DRLG
EDC-48 | 5.5.24 | Makeup Cathead | Observed the make-up cathead line is a chain that needs to be replaced with a wire rope of a proper size (to prevent fall energy and pendulum effect) where it will be difficult to be inspected and detect any defects, require to be replaced immediately | Critical | Reliable Securing REV04, API RP 54, IADC HSE Guidelines | Open | RA-3 | DRLG
EDC-48 | 5.9.7 | Rig Clinic | Only one PAD SET FOR AED (automated external defibrillator) used for CPR in the clinic found expired from 17-4-2023, new valid sets need to be provided ASAP | Critical | WHO, API RP 54, IADC HSE Guidelines | In progress | RA-3 | DRLG
EDC-49 | 2.3.30 | Backup Rotary hose | Backup Rotary hose was founded in bad condition damaged in outer rubber shield, metal shield exposed and corroded, require to be replaced. Moisture will enter into the reinforcement materials, and there are no existing means available to remove it. As a result, corrosion will occur to the reinforcement materials, which over time, will progress to the point where the strength of the reinforcing materials will be reduced, and the pressure integrity and useful life of the hose will be compromised. | Critical | API RP 7L_AD2 SEC. A6 | In progress | FCS-2 | DRLG
EDC-50 | 1.6.2 | Top Drive | Interlock safety system related to movement of link tilt in place but not activated due to an conjunction mechanical and electrical failure, HIPO of collision incident with monkey board may occurred by unintentional human mistake and may lead for several of sever injures cases or fatality which is highly recommended to repair and reactivate the safety system. | Critical | , API Spec 8A, Spec 8C & RP 8B, ,NATA or SI 2307,LOLER | Open | RA-2 | DRLG
EDC-50 | 3.3.17 | Choke manifold remote control panel | While perform F/T to choke manifold remote control panel, hydraulic oil severe leaking observed, in need to be concerned and maintained immediately. | Critical | OEM API RP53, API spec 16C, API 16D, API RP16E, API RP 570 | In Progress | FCS-3 | DRLG
EDC-50 | 4.3.92 | Shale Shakers | Shale Shaker # 3 and 4 plug and receptacle located at shaker tank are not Explosion proof type , need to be replaced ASAP with EX type | Critical | API RP 500/505 , API RP 14FZ , IADC HSE Guide Lines | Open | RA-3 | DRLG
EDC-50 | 4.3.94 | 3rd Party Centrfuge | 3rd party Centerfuge pump power cable running to control panel without gland need to instal Ex gland to maintain the integrity of EX. Protection | Critical | API RP 500/505 , API RP 14FZ , IADC HSE Guide Lines | Open | RA-3 | DRLG
EDC-50 | 4.5.25 | SCR | Ground fault detector need to equipped with visible & sound alarm | Critical | API RP 14FZ API RP 14F API RP 500/505 IEC-60079 | Open | FCS-1 | DRLG
EDC-50 | 4.11.67 | kitchen | Galley exhaust area is not clean and exhaust filter not exist, also motor outside missing covers. | Critical | IADC HSE Guide line API RP 54 | Open | RA-2 | DRLG
EDC-50 | 4.11.73 | catering caravan | Water Heater Elec. Cover is loose and need to be fixed to avoid Elec. Shock. | Critical | API RP 14FZ API RP 14F API RP 500/505 IEC-60079 | Open | RA-2 | DRLG
EDC-50 | 5.5.129 | Centrifuge Unit | Centrifuge unit observed as unsafely working area totally where: missing for guardrails while it is running at height elevation may lead to personal falling any time, two bolts of its base which fixing the centrifuge equipment observed not tied properly although it is vibrator equipment which may lead to suddenly losing any time, crack also bindings observed along its base, slope gritting observed, a gap between its ladder and working area observed and also its main power cable observed cut. all previous reasons have to be considered and the equipment should be maintained or replaced to avoid any undesirable incidents | Critical | IADC HSE Guidelines API RP 54 | Open | RA-3 | DRLG
EDC-50 | 5.5.132 | Mud System | All mud system grating observed damaged in parts also non elevated in somewhere, not fixed properly somewhere, obstructions observed somewhere, require deep repairing and colored with caution color (yellow and black) especially the butterfly valves to prevent any tripping, slipping hazards | Critical | OSHA 1910.23(c)(1) IADC HSE Guidelines API RP 54 | Open | RA-3 | DRLG
EDC-50 | 5.5.139 | Fall Protection System | The fall protection system used not match the standard personnel securing requirements, where: fall arrestor device anchored on derrick ladder used for climbing the first section of the derrick ladder then the derrick man take off this system and use the carbineer system from the 2nd section while stand on the derrick ladder which may lead to personnel falling hazard. The fall protection system should reach to the rig floor. | Critical | IADC HSE Guideline (2015) chapter 20 OSHA 1926.502 OSHA 1910.140 | Open | FCS-3 | DRLG
EDC-50 | 5.5.155 | Fall Protection System | Observed that: the derrick man using only Derrick climber (climb assist device) as a fall protection securing method, while it is just to be used to minimize the climber energy produced during climbing so, a fall arrest system should be provided and used as a fall protection securing while climbing the derrick. | Critical | New updated EDC Safety Manual Ch.4 Working at Heights, Appendix (E): Ladders & Stairs (Derrick ladder) | Open | RA-3 | DRLG
EDC-50 | 5.5.156 | Climb Assist Device | Derrick climber (climb assist device) wire observed in poor condition where strand separated from each other’s in somewhere (the core protruding) also it observed rusty and corroded. | Critical | API RP 9B EDC Safety Manual | Open | RA-3 | DRLG
EDC-50 | 5.6.85 | Makeup Cathead | The make-up cathead line is a chain that needs to be replaced with a wire rope of a proper size (to prevent fall energy and pendulum effect) where it will be difficult to be inspected and detect any defects, require to be replaced immediately | Critical | Reliable Securing REV04, API RP 54, IADC HSE Guidelines | Open | FCS-3 | DRLG
EDC-50 | 5.6.98 | BOP Crane | Observed the BOP Crane lines are a chain that needs to be replaced with BOP Crane attached with a wire rope (to prevent fall energy and pendulum effect) where it will be difficult to be inspected and detect any defects. | critical | Drops Reliable Securing REV04 | Open | RA-3 | DRLG
EDC-50 | 5.7.39 | Diesel Fire Pump | There is no Diesel Fire Pump in main camp to be used while emergency, need to be provided soon according to Updated EDC Safety Manual | critical | Updated EDC Safety Manual Ch.11 (Fire protection and Prevention) | Open | RA-3 | DRLG
EDC-54 | 1.2.6 | Derrick Structure | There is a replaced portion of the flange of 2 beams in the set-back area and the replaced was done by a small thickness plate than the original one -Need To confirm with the OEM if this is safe to operate especially this is under set-back area and subjected to direct load of tubulars weight. | Critical | 0 | In Progress | FCS-1 | DRLG
EDC-54 | 1.2.8 | Raising lines | The raising lines certificates, which submitted to us from 2013, and there is no clear history for the time life or numbers of cycles for the Mast raising lines, the first inspection was in 2018. The rig not used the raising lines since May, 2021. While they carried out the rig move by towing, the rig head plan to use raising lines in next rig move due to they will dismantling the rig , so we need clear statement of fact from EDC about the numbers of cycles and the time life for the exits raising lines before next rig move. | Critical | IADC, API Spec 4E, 4F,BS12385-4 | Open | FCS-3 | DRLG
EDC-54 | 1.3.19 | DW | There is medium water leak on DW brake ram O.D. S need to check ASAP by maintenance team to avoid slipped brake with excess weights | Critical | ADC, API RP 9B, API 9A ,API 7K ,API7L | Open | RA-3 | DRLG
EDC-54 | 1.6.8 | TDS 11 SA | There is mechanical deflection and twist in the lower section for TDS Guide, this could be lead to accident during TDS carrier moving, need to repair and inspect with Third party company ASAP. | Critical | OEM,IADC, API Spec 8A, Spec 8C & RP,8B | Open | FCS-3 | DRLG
EDC-54 | 3.1.19 | BOP HPU | There 3 ea. Control hoses damaged in outer shield which connected to BOP, required to be replaced. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | In Progress | RA-2 | DRLG
EDC-54 | 3.2.13 | BOP | There 5 ea. Control hoses damaged and have series outer shield cutting which connected to BOP, the open line for blind ram rejected and have to replace immediately,it's completely worn out and rusted wire and started leaking oil, no way to use any more, required to be replace | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | In progress | FCS-3 | DRLG
EDC-54 | 5.6.164 | 0 | Pins secured the V-DOOR posts at rig floor noticed the pins diameter not matched with pad eye hole. Highly recommended to replace the pins | Critical | LOLER 1998 regulations AS 1380 | open | FCS-3 | DRLG
EDC-54 | 5.7.34 | 0 | Climb assist device's wire anchored incorrectly where: it is not anchored in pad eye (capable of supporting at least 5000 pounds (2268 kilos)per employee) (just wrapped around iso corner of kommey) also the used wire without thimble (hard eye) and observed in a poor condition.Then, the wire should be replaced by another one also anchored in pad eye that capable of supporting at least 5000 pounds and MPI and load test performed for it. | critical | OSHA 1910.27(b)(1)(i) IADC 20.3.C API RP 9B | open | RA-3 | DRLG
EDC-54 | 5.7.35 | 0 | Observed the make-up cathead line is a chain that needs to be replaced with a wire rope of a proper size (to prevent fall energy and pendulum effect) where it will be difficult to be inspected and detect any defects. | Critical | Reliable Securing REV04, API RP 54, IADC HSE Guidelines | In progress | RA-3 | DRLG
EDC-54 | 5.9.120 | 0 | Highly greased oil observed accumulated below the Kitchen fryer present a serious fire hazard, require a deep cleaning and to be cleaned periodically | critical | API RP 54, NFPA 72 NFPA 30, OSHA 1910.106 | open | RA-3 | DRLG
EDC-57 | 1.1.42 | Kelly Hose |  | Critical | API RP 7L_AD2 SEC. A6 | Open | RA-3 | DRLG
EDC-57 | 3.2.15 | SGL Ram | Single ram MFD is 10 Aug. 2018 and recertification shall be after 5 years at 10 Aug. 2023 EDC submitted certificate of extension COC which require to be SOF certificate include field report with all activity done such as NDT, Measurements….etc. for equipment. AS per API 16AR Annex C table : - Description of the work done. - Pressure tests records. - Disassembly records. - Origin and serial numbers of parts replaced. | Critical | API 16AR Annex C | Open | RA-3 | DRLG
EDC-57 | 5.9.42 | ## | Kitchen ventilation hood shows excessive grease from inside hood, outside duct and filters presenting a serious fire hazard which require an immediate cleaning and to be directed for a monthly cleaning schedule. | Critical | API RP 54 7.1, NFPA 30 | Open | FCS-2 | DRLG
EDC-58 | 0.5.5 | ## | There is no coc or load test certificates submitted for life saving posts which located on monkey board and crown ,the anchorage point must be capable of supporting at least 5000 pounds (2268 kilo) per employee | Critical | OEM,IADC HSE GUIDELINES CH 20.3C | in progress | RA-3 | DRLG
EDC-58 | 4.8.40 | Diesel Tank | Fuel Purifier AC motor is not Explosion Proof type need to be replaced by EX type motor. | Critical | API RP 505 8.2.1.3.1 , NFPA 30 ,IEC 60079-10 | In progress | RA-3 | DRLG
EDC-58 | 5.1.167 | ## | Observed deep hole in front right tire for forklift reached to 2 CM ,should to be replaced immediately according to IADC HSE GUIDELINES Ch.9 (Gouges or large chunks missing from tires) | CRITICAL | IADC HSE GUIDELINES CH 9 | Open | RA-3 | DRLG
EDC-58 | 5.2.70 | Main Camp | Safety Fixed guard for dough mixer is missing which could lead to contact of operator with rotating parts | Critical | OEM, EN 453:2014 | in progress | FCS-3 | DRLG
EDC-61 | 4.4.7 | TDS | TDS interlock between Link-Tilt & Pipe Handler isn't working | Critical | IADC HSE Guide line API RP 54, NEC 314.24 | open | RA-2 | DRLG
EDC-61 | 4.13.44 | Bakery Room | Bakery Oven is in Very Bad Condition, door broken, door seal is damage, side cover is not properly closed, thermostate is not Function (no cut out) | Critical | HSE Guidline/OEM | In progress | RA-2 | DRLG
EDC-61 | 5.7.23 | ## | Observed the BOP Crane lines are a chain that needs to be replaced with BOP Crane attached with a wire rope (to prevent fall energy and pendulum effect) where it will be difficult to be inspected and detect any defects. | critical | Drops Reliable Securing REV04 EDC Safety manual QM-LEVEL2 (5.4.5.4 Chain Hoists) | Open | RA-3 | DRLG
EDC-61 | 5.10.32 | ## | There is no PAD SETS FOR AED (automated external defibrillator) used for CPR in the clinic, only one set exists and found expired from 11-8-2022 | Critical | WHO, API RP 54, IADC HSE Guidelines | Open | RA-3 | DRLG
EDC-62 | 3.2.13 | Single Ram | SGL ram was found expired, required to be replaced with new SGL certified, MFD 18 Feb. 2018. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-3 | DRLG
EDC-62 | 4.2.28 | MCC | Found Clear AC Ground Fault in MCC , need to find the defected grounded equipment and clear the fault ASAP | Critical | OEM/PMS | Open | FCS-3 | DRLG
EDC-65 | 3.2.9 | BOP Stack | DBL ram, found top ram had oil leakage from operating pistons while closing at both sides, blind ram found same moreover top ram pistons rod had wear and corroded. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | DRLG
EDC-65 | 3.2.10 | BOP Stack | Top ram hang of pin found oil leakage from its seals, require to be changed. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | DRLG
EDC-65 | 4.5.39 | Shale shaker #2 | Vibrator Motor J.B is damage and not installed properly ,it doesn’t maintain the integrity of EX.Protection , high risk for mud to enter to Motor J.B which can cause fire and short circuit. | Critical | API RP 14FZ 12.3.7 API RP 14FZ 16.3.5 IEC-60079 OEM | Open | FCS-1 | DRLG
EDC-65 | 5.7.35 | 0 | Found the type of makeup torque wire rope sling that attached to cathead is hard end to plain end secured by three clamps type U-Bolt Clamp, Need justification for this type of wire rope sling and clamps if it suitable to fit the maximum torque with safe factor which can achieve using cathead safely or replacing by hard end to hard end wire rope sling to avoiding slipping rope through clamps, rapid fatigue and in case of mechanical failure. According to rig manual not mentioned the type of wire sling. | Critical | OEM | open | FCS-1 | DRLG
EDC-65 | 5.7.39 | 0 | Man riding winch not equipped with auxiliary air tank for (emergency disc brake release) as per the winch manual recommendation for emergency lowering in case of loss the air supply.( Man riding winch S.N: KG0001928 / Model No: FA150KGMR/01014) | Critical | OEM | In progress | FCS-1 | DRLG
EDC-65 | 5.7.40 | 0 | Multiple fail finding at the monkey board auxiliary escape system as following: A- Device far away from monkey board platform this makes it difficult to allow the user to mount the unit. C- No gate in the work platform guard railing for safe and effective exiting. D- Old type of device in place which is not allow the user to secure himself with device. Recommend proper rigging up for device, make the device reachable for user, provide the platform with gate for effective and safe exiting and provide the rig with new version of escape device allow the user to secure himself with it. | critical | OEM, API RP 54 6.12, IADC HSE Guidelines 3.15 | open | FCS-1 | DRLG
EDC-75 | 4.3.40 | IBOP interlock | IBOP interlock system with MP's NOT available | Critical | OEM/IADC HSE guide line safety recommendation | Open | FCS-1 | DRLG
EDC-75 | 4.9.3 | UPS | 1-Rig sense DAQ should be power through UPS to provide continuous monitoring of proper reading for drilling parameters data to help driller to take proper decision in case of any well control issues or power loose such as following: - CCTV system should be powered through UPS to provide continuous monitoring and recording of all Cameras positions in case of blackout or power loss to help all key persons to take proper decision in case of any emergency case or somebody stuck on monkey board or stabbing board -Fixed Gas detection system and warning alarms of the fixed fire detection/fighting system should be powered through UPS to provide continuous monitoring for GAS level values for H2S/LEL and help in taking proper and fast action in case of gas release - Rig communication and Paging system should be powered through UPS to provide continuous power supply in case of blackout or power loss and provide continuous communication between rig Crew and to announce any emergency or evacuation cases. | critical | API RP 14F section 10.5,API RP 540 section 9.4.2.2 OEM/PMS | Open | FCS-2 | DRLG
EDC-75 | 5.7.22 | 0 | Multiple of safety features and others at man riding malfunction such as: - Air Regulator leaking. - Slack Wire detector Malfunction. - Stainless Steel Slack Wire Arm Loose. - Emergency lowering system Malfunction. | Critical | OEM | In progress | FCS-2 | DRLG
EDC-75 | 4.5.50 | Diesel tank | Fuel purifier AC motor is not Ex-Type , need to replace it with Ex-Type motor ASAP. | Critical | API RP 500/505 , API 14FZ | Open | RA-2 | DRLG
EDC-82 | 5.5.4 | Man Rider | No man raider available ,it’s not safe to use man basket and HYD winch winches. | critical | IADC HSE guidelines | Open | FCS-1 | PU
EDC-83 | No Critical | No Critical | No Critical | No Critical | No Critical | No Critical | No Critical | WO
EDC-84 | 3.1.11 | BOP HPU |  | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-3 | WO
EDC-84 | 5.6.105 | ## | Totally Poor installing for Crown fall arrest system which used as a fall protection system on derrick ladder, where it is should not attached to guardrail because guardrail is not built to withstand the impact forces generated by a fall, also there is no second pad eye to be used to secure the arrestor as a 2nd retention | Critical | IADC HSE Guideline (2015) chapter 20.3.c & OSHA 1926.502 | Open | FCS-3 | WO
EDC-87 | 0.2.2 | ## | No load test carried out for the man life post at the monkey board which is require to carry out a load test by 3rd party and must be capable of supporting at least 5000 pounds (2268 kilos)per employee also the MPI test to be conducted before and after the load test. | Critical | IADC HSE Guidelines 20.3 C | Open | RA-2 | WO
EDC-87 | 1.1.38 | Power swivel | Found the ESD button for the power swivel was broken and not functioned which is should be repair or replace for continuous safe operations. | Critical | OEM, API 500 | Open | FCS-3 | WO
EDC-87 | 5.7.53 | ## | Improper anchoring for the fall arrestor at the crown section due to it anchored at the derrick ladder rungs which is should provide the mast with separated pad eye for anchorage point and must be capable of supporting at least 5000 pounds (2268 kilos)per employee also FYI most standard guardrail systems are not adequate anchorage points because they are not built to withstand the Impact forces generated by a fall. | critical | IADC HSE Guidelines 20.3 C | open | RA-2 | WO
EDC-87 | 5.7.59 | ## | During the F/T of man riding safety features are found the slack wire detector malfunction. | Critical | OEM | Open | FCS-3 | WO
EDC-88 | 3.1.17 | BOP Hydraulic power unit | Electrical triplex pump, fluid end oil seals found damaged and there is hydraulic oil leaking in triplex pump pan. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | In Progress | RA-3 | WO
EDC-88 | 4.5.11 | Grounding |  | Critical | IADC HSE Guid line API RP 54, IEEE std 142, NEC table 250-66, NFPA 70 , API RP 540 | Open | FCS-3 | WO
EDC-88 | 5.5.4 | ## | Fall arrestor located at the crown section anchored with welded pad eye at the crown section guardrail even though standard recommended for guardrail systems are not adequate anchorage points because they are not built to withstand the Impact forces generated by a fall. Statement of fact from manufacture with full specification of that pad eye are require or providing the crown section with adequate and suitable anchorage point and must be capable of supporting at least 5000 pounds (2268 kilos) per employee. | critical | IADC HSE Guidelines 20.3 C | open | FCS-3 | WO
EDC-89 | No Critical | No Critical | No Critical | No Critical | No Critical | No Critical | No Critical | WO
EDC-90 | 1.5.5 | Swivel |  | Critical | No Reference | In progress | FCS-3 | WO
EDC-90 | 3.1.26 | Closing unit | Hydraulic hose kill line contained a mechanical defection such as kinks, crushed sections, and cover with excessive damage which exposes reinforcement will eventually break down the reinforcement and lead to a hose failure. | Critical | No Reference | Open | RA-3 | WO
EDC-90 | 3.1.27 | Closing unit |  | Critical | No Reference | Open | RA-3 | WO
EDC-90 | 3.2.13 | Choke Manifold | Found choke manifold (upstream) rated working pressure is 5000 psi while the rig BOP stack rated working pressure 10000 psi, not complying to API STD where the choke or BOP RWP shall be equal or exceed the MASP for the well program | Critical | No Reference | Open | RA-2 | WO
EDC-90 | 4.7.24 | Main camp | Main Freezer unit does not have ELCB earth leakage circuit breaker need to install it ASAP | Critical | No Reference | In progress | FCS-3 | WO
EDC-90 | 4.12.5 | Grounding |  | Critical | No Reference | open | FCS-1 | WO
EDC-90 | 5.5.10 | ## | Crown Fall arrestor that used as derrick ladder fall protection system observed anchored on guardrail that not adequate anchorage point because it is not built to withstand the impact force generated by a fall, post of two bad eyes each one capable of supporting at least 5000 Ib need one used as anchorage piont for arrestor and the other used as a 2nd retention for it | Critical | No Reference | open | RA-3 | WO
EDC-90 | 5.9.83 | Clinic | The two PAD SETS FOR AED (automated external defibrillator) used for CPR in the clinic found expired from 17-4-2023 | Critical | No Reference | open | FCS-3 | WO
EDC-91 | 1.2.12 | Mast | D.S Mast telescopic cylinder piston leaking from lower seal. | Critical | IADC , 8A, 8C & RP 8B, API RP53, API RP54 | Open | RA-2 | WO
EDC-91 | 1.2.16 | Mast | There is cutting and damaged in outer shield rotary hose at stand pipe line | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | RA-3 | WO
EDC-91 | 1.3.1 | Crown | Manufacturer’s specification/operation plate is not attached to crown block, so there is no any link between the paper work/ certificates and the block. | Critical | API RP 7L 1.4.2 API Spec 8A, 8C & RP 8B | In Progress | FCS-1 | WO
EDC-91 | 2.4.23 | MP | Mud pump Relief line its low presser pipe and thread and connection not stander must be high pressure schedule 80 with hammer union 1502 | Critical | OEM, API 500, API RP 7C-11F | Open | FCS-3 | WO
EDC-91 | 3.3.16 | BOP HPU | Closing unit remote panel, found not connected and not in its correct location which require to move near STP office. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | RA-3 | WO
EDC-91 | 3.3.23 | BOP Hydraulic Power Unit – HPU |  | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | RA-3 | WO
EDC-91 | 3.3.24 | BOP Hydraulic Power Unit – HPU | Electrical triplex pump, fluid end oil seals found damaged and there is hydraulic oil leaking in triplex pump pan. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | RA-3 | WO
EDC-91 | 3.5.15 | Choke remote panel | Choke remote panel (Swaco panel) mulfunction due to air regulator not installed.in need to maintain or replaced. | Critical | OEM API RP53, API spec 16C, API 16D, API RP16E, API RP 570 | Open | RA-3 | WO
EDC-91 | 5.2.22 | Fall arrestor | Proof load test carried out on the fall arrest pad eye at the crown not meet the proper requirment capacity as per the IADC requirment which is only tested for 1Ton anchorage point related to personal fall prevention must be capable of supporting at least 5000 pounds (2268 kilos)per employee, it's built to withstand the Impact forces generated by a fall. | critical | IADC HSE Guidelines 20.3 C | Open | FCS-3 | WO
EDC-91 | 5.2.28 | Crown fall Arrestor | Totally improper installing for Crown fall arrest system which used as a fall protection system on derrick ladder, where it is should not attached to guardrail because guardrail is not built to withstand the impact forces generated by a fall, a post attached with 2 pad eyes (One for arrestor hold and the other used to securing the arrestor) of certified load capacity 5000 Ib (Load test certificates) should be provided instead. | critical | IADC HSE Guideline (2015) chapter 20.3.c & OSHA 1926.502 | Open | RA-3 | WO
EDC-91 | 5.2.29 | DS winch | (DS) winch's wire observed in poor condition where observed that: -It is broken in some parts - The whole wire is rusty The wire need to be re-inspected by 3rd party company or replaced by another one to avoid different hazards | Critical | API RP 9B, BS EN 13414, EDC Safety Manual | Open | RA-3 | WO
EDC-91 | 5.4.20 | Escape Device | Totally improper installing for Auxiliary Escape device (Geronimo) especially the anchor point from mast side also the counter balance anchor point on ground both of them need to be anchored referred to standards and OEM also there is no load test carried for the pad eye of dead man anchor point which is shall the anchorage point must be capable of pulling at least 3000 pounds, it's built to withstand the Impact forces generated by a fall. | Critical | OEM, API RP 54 6.12 IADC HSE Guidelines 3.15 | Open | FCS-3 | WO
EDC-92 | No Critical | No Critical | No Critical | No Critical | No Critical | No Critical | No Critical | WO
EDC-93 | 2.5.11 | High pressure lines |  | Critical | API RP 7L_AD2 SEC. A6 | Open | FCS-3 | WO
EDC-93 | 2.5.15 | High pressure line | There is welded plate installed for High pressure line, not allowed to welding over high pressure lines body. | Critical | API RP 7L, ASME | Open | RA-3 | WO
EDC-93 | 3.3.17 | Choke manifold | Choke manifold MFD which stampped over valves name plates is May 2018 which require to perform CAT IV for choke manifold. | Critical | OEM API RP53, API spec 16C, API 16D, API RP16E, API RP 570 | Open | RA-3 | WO
EDC-93 | 4.3.5 | UPS | All the following loads should be power through UPS to provide continuous power supply incase of power loss or black out: 1- Instrumentation DAQ and Driller HMI to provide continuous storage for Data , calibration and monitoring for and drilling parameters . 2- Fixed Gas Detection system and Alarm system to provide continuous monitoring for gas levels and also alarm incase of any emergency gas release cases. 3- BCS system. 4- Rig communication and Paging system should be powered through UPS to provide continuous power supply in case of blackout or power loss and provide continuous communication between rig Crew and to announce any emergency or evacuation cases. 5- CCTV system should be powered through UPS to provide continuous monitoring and recording of all Cameras positions in case of blackout or power loss to help all key persons to take proper decision in case of any emergency case or somebody stuck on monkey board or stabbing board | Critical | API RP 14F , API RP 14 FZ section 10.5 | Open | RA-3 | WO
EDC-93 | 4.5.26 | Dog House | Gas Detection Monitor installed on dog house in OFF Mode , need to troubleshoot and fix and ensure that it is always in ON Mode and all Sensors reading is monitored | Critical | IADC HSE Guide line , API 14-F , OEM/PMS | Open | RA-3 | WO
EDC-93 | 5.9.37 | Kitchen-Mian Camp | Kitchen ventilation extractor and internal and outer duct shows excessive grease which present a serious fire hazard and require to be cleaned. | Critical | API RP 54, NFPA 72 | open | FCS-2 | WO
EDC-93 | 5.9.61 | Kitchen | The catering crew hygiene performance is very weak and no one trained on the catering and food serving principles which require training for hygiene, food servicing, food storing, defrosting practices and housekeeping awareness.(The same observations noticed while the 2nd RA therefore the majority upgraded to critical) | Critical | API RP 54, IADC HSE Guidelines. | Open | FCS-2 | WO
EDC-93 | 5.10.21 | CM Office Skid | Found deep hole in side left rear tire for Co.Man office skid ,require to be changed immediately before rig move to avoid explosion hazard | Critical | IADC HSE CH 9 | Open | FCS-3 | WO
EDC-95 | 3.1.23 | BOP HPU | BOP HPU Control lines, found some of coflex hydraulic hoses are having hard hits, damaged and collapse, in need to be replaced by outer metal shield (Highly recommended). | Critical | IADC, API RP53, API RP54, API 16D, API RP16E& API 16A | In progress | FCS-3 | WO
EDC-95 | 3.1.24 | BOP HPU | BOP control lines, found all hoses equipped with quick release connection while not allowed to using it, so in need to replace with union quick coupler. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-3 | WO
EDC-95 | 3.3.18 | Choke Manifold | The chock hose installed with small diameter at chock manifold side, the chock line should be at least equal in diameter to the choke valves, This line allows circulation of the well with the preventers closed while maintaining a minimum of backpressure. It also permits high volume bleed-off of well fluids to relieve casing pressure with the preventers closed. | Critical | API RP 53 SEC 8.3.1.C5 ,IADC Drilling Manual V.3.8 Figure K1-2E | Open | RA-3 | WO
EDC-95 | 4.3.25 | Power House | fixed gas system not reading shale shaker sensors ( H2S , LEL ). Need to be repaired as soon as possible | Critical | API RP 540 5.4.1/RP14FZ API RP 14F/RP500-505 IADC HSE Guide line IEC-60080 | Open | RA-3 | WO
EDC-95 | 5.6.127 | Mud Pump Carrier | Observed 3 tires at mud pump carrier in poor condition and worn out because was found deep holes and cutting in different parts, should to be changed before rig move to avoid incidents | Critical | IADC HSE CH 9 O | Open | RA-3 | WO
EDC-95 | 5.9.3 | Rig Location | Lifting person by air winsh not accepted very risky must be use man-riding machine .(safety instruction)However the crew make Deviant primet to use air winsh (NOT protected the life of person). | Critical | IADC HSE GUIDELINES and EDC safety manual | open | FCS-1 | WO
EDC-97 | 1.1.37 | Crane 60 ton | Mobile crane with SWL 60T / S.N: 80940 found the operational engine turbo charger accumulated with oil also there is marks showed of medium oil leak which is may lead for HIPO of fire hazard. Highly recommended for repairing or replacement. | Critical | OEM, IADC, API RP 54 | Open | FCS-3 | WO
EDC-97 | 1.1.39 | Power tong | Power tong hydraulic hose contained a mechanical defection such as kinks, crushed sections, and cover with excessive damage which exposes reinforcement will eventually break down the reinforcement and lead to a hose failure. | Critical | API PR 7L | Open | FCS-3 | WO
EDC-97 | 1.2.4 | Mast Structure | Deflected back beam (draw work side) bowed (deflected) size of bow 11 mm at mid-point near upper flange and 16 mm at mid-point of the lower flange, beam length 223cm, Code API RP rejection criteria 12mm over 10 ft. and by calculation for 223 cm the tolerance will be 8.5 mm and we are 11 mm and 16 mm | Critical | API RP 4G | Open | FCS-1 | WO
EDC-97 | 1.2.27 | Power Swivel | Power swivel hydraulic hose contained a mechanical defection such as kinks, crushed sections, and cover with excessive damage which exposes reinforcement will eventually break down the reinforcement and lead to a hose failure | Critical | API 500,OEM | Open | FCS-3 | WO
EDC-97 | 2.6.6 | fire pump | Engine radiator of fire pump had no cap and the neck is broken and corroeded morover the return line of water coolant missed its clamp | critical | OEM,API 500, IADC HSE CH 5 | Open | RA-3 | WO
EDC-97 | 3.2.12 | BOP double ram | Double ram, blind ram found hing of pin had oil leake | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | In progress | RA-3 | WO
EDC-97 | 3.2.13 | HCR Control line | Chok line valve control hose found damaged in outer metal chield. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | RA-3 | WO
EDC-97 | 4.1.7 | Water treatment | Chlorine pump at water treatment is malfunction. | Critical | IADC HSE Guideline ,OEM | In progress | FCS-2 | WO
EDC-97 | 5.6.69 | Hydraulic Tagger | Using hydraulic tagger for lifting personnel as there is no man rider winch. | critical | IADC HSE GUIDELINES | Open | FCS-1 | WO
EDC-97 | 5.6.124 | Rig Floor | Sub-standard height of the guardrail placed at rig floor and directly front of the telescopic cylinder of mast approximately (50cm) from rig floor which recommend for adjusting the height as per standard recommendations to avoid HIPO of falling hazard may lead for severe injury. | critical | IADC HSE Guide Lines Ch 3.11 | Open | FCS-3 | WO
EDC-97 | 5.7.19 | Makeup torque | Make up torque wire rope sling in place type is thimble eye in one end and plain other end and the recommended wire rope sling to be in place as the rig manual recommendation to be thimble eye in the both ends also found improper type of clamps used and improper method of clamping. | critical | OEM | open | FCS-3 | WO
EDC-97 | 5.7.20 | Monkey Board | Multiple fail finding at the monkey board auxiliary escape system as following: A- Escape device rigged up on wire rope sling in inverse position. B- Device far away from monkey board platform this makes it difficult to allow the user to mount the unit. C- No gate in the work platform guard railing for safe and effective exiting. D- Old type of device in place which is not allow the user to secure himself with device. Recommend proper rigging up for device, make the device reachable for user, provide the platform with gate for effective and safe exiting and provide the rig with new version of escape device allow the user to secure himself with it. | critical | OEM, API RP 54 6.12, IADC HSE Guidelines 3.15 | open | FCS-3 | WO
EDC-97 | 5.7.24 | Forklift | During the deep inspection carried out on forklift noticed deep and major side cut at the inner side of front left tire and classified as HIPO of explosions' Forklift with S.N:22Z03951. | Critical | IADC HSE Guidelines Ch.9 , EDC Onshore Contingency Manual QM Level-3 | Open | FCS-3 | WO
EDC-97 | 5.7.31 | Mobile Crane | During the deep inspection carried out on mobile crane noticed long, deep and major side cut at three tires two tire at left side and one tire at right side thus, it will classified as HIPO of explosions' Mobile crane S.N:80940. | Critical | IADC HSE Guidelines Ch.8 & OEM | Open | FCS-3 | WO
NDC-4 | 4.2.8 | Mast | BCS (Anti Collision System) is Not Available (crown-floor saver) | Critical | IADC HSE Guide line | Open | FCS-1 | WO
SDF-1 | 1.1.7 | Kelly Hose | Rotary hose (Kelly hose) found in very bad condition, damaged in outer shield, second layer damaged, require to be changed. | Critical | API RP 7L_AD2 SEC. A6 | Open | FCS-1 | WO
SDF-1 | 1.1.13 | Brake Band | DW CAT III inspection for DW brake, missed inspection on the brake band and brake band pins, the inspection performed for equalizer beam and brake lever. | Critical | OEM,IADC, API RP 7L, RP 570 | Open | FCS-1 | WO
SDF-1 | 1.1.14 | Power tong | Power tong safety door mechanism found its hoses is not connected, require to be connected and perform FT. | Critical | OEM,IADC, API RP 7L, RP 570 | Open | FCS-1 | WO
SDF-1 | 2.1.7 | Camp engine no.2 | There is diesel leaking at main camp engine no. 2 from diesel lines and diesel injector lines, all diesel leakage require to be fixed. | Critical | IADC HSE guidelines Ch.5 | Open | FCS-1 | WO
SDF-1 | 2.3.5 | MP | Mud pump relief line found had 2 coupling 3" thread type, high pressure line shall not using thread connection more than 2". | Critical | API RP 53, API RP 54 | Open | FCS-1 | WO
SDF-1 | 2.3.6 | MP | Mud pump PRV found size 3" thread type, high pressure line shall not using thread connection more than 2". | Critical | API RP 53, API RP 54 | Open | FCS-1 | WO
SDF-1 | 2.3.7 | MP | High pressure hose (vibrator hose) which connected between mud pump and surface line in poor condition damaged in outer rubber shield in several spots and slipped out from its place and found metal shield is exposed and corroded. Moisture will enter into the reinforcement materials, and there are no existing means available to remove it. As a result, corrosion will occur to the reinforcement materials, which over time, will progress to the point where the strength of the reinforcing materials will be reduced, and the pressure integrity and useful life of the hose will be compromised. | Critical | API RP 7L_AD2 SEC. A6 | Open | FCS-1 | WO
SDF-1 | 2.4.4 | 0 | Vibrator hose between stand pipe and surface line found in very bad condition require to be changed. | Critical | OEM, IADC, API Spec 7K, RP 7L & API RP 570 | Open | FCS-1 | WO
SDF-1 | 3.1.1 | BOP HPU | The BOP control system found accumulator compartment divided for only 2 compartment not comply with API Specification 16D section 5.1.3.2 which stated that the accumulator system should be designed as such so that the loss of an individual accumulator or bank would not result in more than 25% loss of the total accumulator system capacity. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | WO
SDF-1 | 3.2.2 | BOP | Kill line manual valve MFD as mention in certificate is 2010 which require perform CAT IV overhauling. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | WO
SDF-1 | 3.2.3 | BOP | Kill line one way valve MFD as mention in certificate is 2014 which require perform CAT IV overhauling. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | WO
SDF-1 | 3.2.4 | BOP | HCR manual valve MFD as mention in certificate is 2010 which require perform CAT IV overhauling. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | WO
SDF-1 | 3.2.5 | BOP | HCR Hydraulic valve MFD as mention in certificate is 2014 which require perform CAT IV overhauling. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | WO
SDF-1 | 3.2.6 | BOP | HCR hose found thread type and welded, moreover the hose found not fire resistance. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | WO
SDF-1 | 3.3.1 | Choke Manifold | Choke manifold consist of 3 ea. Valves and 1 adjustable manual choke, as per API RP 53 for 5K choke manifold as mention require to be consist of 1 remotely operated choke and manual adjustable choke. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | WO
SDF-1 | 3.3.2 | Choke Manifold | Choke manifold valves missed name plate, and there is no COC for choke manifold. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | WO
SDF-1 | 4.1.2 | Diesel Pump | Gland of diesel pump AC motor is broken, wires exposed from junction box and there is diesel and dirt accumulated on cable and wires | Critical | API RP 505 8.2.1.3.1 , NFPA 30, IEC 60079-10 | Open | FCS-1 | WO
SDF-1 | 4.1.6 | Diesel / Water Tank | There is no ground connected to diesel tank at all. | Critical | API RP 540 5.5.2/RP14FZ API RP 14F/RP500-505 IADC HSE Guide line IEC-60079 OEM | Open | FCS-1 | WO
SDF-1 | 4.2.2 | Gen #1,2 | Both Generators missing grounding from body of generator to standard ground bolt at engine room skid | Critical | API RP 540 5.5.2/RP14FZ API RP 14F/RP500-505 IADC HSE Guide line IEC-60079 OEM | open | FCS-1 | WO
SDF-1 | 4.3.1 | Mud pump | Main Control panel of mud pump missing most of bolts and it dose not maintain the integerity for EX. Proof. | Critical | API RP 14FZ 6.8, API RP 540, API RP 505 10.4.4.2 | open | FCS-1 | WO
SDF-1 | 4.3.3 | Mud pump | Liner wash AC motor not EX type, need to be replaced by Ex motor classified Zone 2 | Critical | API RP 505 10.4.4.2, API RP 14FZ, API RP 540, OEM | open | FCS-1 | WO
SDF-1 | 4.4.1 | Mud Mix | Gland of mud mix pump AC motor is not EX type and it does not maintain the integrity for EX. Proof. | Critical | API RP 14FZ, API RP 540, API RP 500/505 | Open | FCS-1 | WO
SDF-1 | 4.4.4 | Mud Mix area | Mud agitators Ex junction box placed at mud mix area has an open hole at top of junction box | Critical | API RP 14FZ, API RP 540, API RP 500/505 | Open | FCS-1 | WO
SDF-1 | 4.4.5 | Mud Mix area | Ex lighting junction box has a non-Ex type gland and this gland is not suitable size for the cable (Cable is free) | Critical | API RP 14FZ, API RP 540, API RP 500/505 | Open | FCS-1 | WO
SDF-1 | 4.4.8 | Reserve tank area | Ex lighting junction box at reserve tank has unused glands and it does not maintain the integrity for EX. Proof, need to be removed and use Ex blind plug. | Critical | API RP 14FZ, API RP 540, API RP 500/505 | Open | FCS-1 | WO
SDF-1 | 4.4.9 | Reserve tank area | Gland of centrifugal pump AC motor at reserve tank is not EX type and it does not maintain the integrity for EX. Proof. | Critical | API RP 14FZ, API RP 540, API RP 500/505 | Open | FCS-1 | WO
SDF-1 | 4.4.10 | Reserve tank area | Start/Stop junction box at reserve tank has unused gland, missing junction box bolt and loose bolt | Critical | API RP 14FZ, API RP 540, API RP 500/505 | Open | FCS-1 | WO
SDF-1 | 4.6.6 | Rig Floor | Driller cabin light fixture is without gland and instead of gland sillicon sealing is used | Critical | API RP 14FZ, API RP 540, API RP 500/505 | open | FCS-1 | WO
SDF-1 | 4.6.7 | Anti Collision System | ACS (Anti Collision System) is Not available (crown-floor saver) | Critical | IADC HSE Guide line | Open | FCS-1 | WO
SDF-1 | 4.9.4 | Fly Camp | Earth leakage circuit breaker (ELCB) is not available in most fly camp caravans | Critical | API RP 540, NFPA 70 210.8 | Open | FCS-1 | WO
SDF-1 | 4.11.1 | Main Camp | Earth leakage circuit breaker (ELCB) is not available in all main camp caravans | Critical | API RP 540, NFPA 70 210.8 | Open | FCS-1 | WO
SDF-1 | 4.11.19 | Galley | Galley distribution panel is missing earth leakage circuit breaker. | Critical | API RP 540, NFPA 70 210.8 | Open | FCS-1 | WO
SDF-1 | 5.1.9 | 0 | No coc and load test certificate submitted for life saving post located on crown | critical | OEM,IADC HSE GUIDELINES CH 20.3C | open | FCS-1 | WO
SDF-1 | 5.2.1 | 0 | Rig not equipped with fixed gas detection system, require to be provied | critical | API RP 54 6.6, IADC HSE GUIDELINES CH 13.5 | open | FCS-1 | WO
SDF-1 | 5.6.10 | 0 | Most of walkway supports for mud system missing safety pins or bolts and one support bended, that may lead to collapse it | critical | API RP 4G 5.3 | open | FCS-1 | WO
SDF-1 | 5.6.11 | 0 | Full cutting in front left tire in mud system truck,require to be changed | critical | IADC HSE GUIDELINES CH 9 | open | FCS-1 | WO
SDF-1 | 5.6.19 | 0 | Oxygen and acetylene torch not equipped with flash-back arrestor, should to be equipped | Critical | API RP 54 20.4.2 | open | FCS-1 | WO
SDF-1 | 5.6.22 | 0 | Observed portable grinder applying tape to keep the power switch on, should not be modified. | Critical | IADC HSEGUIDELINES CH 3H | open | FCS-1 | WO
SDF-1 | 5.6.24 | 0 | Observed big deep holes in left rear tire for diesel and water tank truck, should to be replaced ASAP | Critical | IADC HSE GUIDELINES 9 | open | FCS-1 | WO
SDF-1 | 5.7.3 | 0 | The rig carrier not equipped with manriding(personnel hoisting, should to be provided ASAP | Critical | IADC HSE GUIDELINES CH 19 | open | FCS-1 | WO
SDF-1 | 5.7.4 | 0 | Fall arrest system not implemented on monkey board and should be provided ASAP because fall arrest system used to arrest an employee in a fall from a working level. It consists of an anchorage,connectors, a body belt or body harness and may include a lanyard, deceleration device, life line | Critical | OSHA 1926.502 | open | FCS-1 | WO
SDF-1 | 5.7.6 | 0 | Observed guyline from monkey board to ground fastened with another guyline which require to attach it directly in padeye as per OEM,Standard | Critical | OEM,API SPEC 9A,API SPEC 4F,IADC HSE CH 17.8 | open | FCS-1 | WO
SDF-1 | 5.7.7 | 0 | Mast ladder not secured: - Nearest ladder step to ground almost 1meter. - HP hose obstructed ladder. - Mast ladder divided to 2 piece. - ladder not equipped with lad safe device. - Upper ladder so far to monkey board. - ladder lead to falling hazard. | Critical | API RP 54 9.3,IADC HSE CH 16.3 | open | FCS-1 | WO
SDF-1 | 5.8.3 | 0 | Fire tank body rusty and was found holes and many welded points, require to be changed | critical | NFPA 25 3.6.7 | open | FCS-1 | WO
SDF-1 | 5.10.7 | 0 | There is no galley chemicals system inside kitchen, should to be equipped for fire protection | Critical | NFPA 13,16 | open | FCS-1 | WO
ST-5 | 2.3.24 | MP No.1 & 2 | Mud pump Cameron gauge for both mud pumps found not flange type. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API RP 570, API 16A | Open | FCS-1 | DRLG
ST-5 | 2.3.28 | Stand pipe | Stand pipe pressure gauge (Cameron gauge) found not flange type. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API RP 570, API 16A | Open | FCS-1 | DRLG
ST-5 | 3.3.34 | Choke manifold | Choke manifold sent for CAT IV overahuling due to COC is expired, the document which submitted not mentioned for any overhauling report only submitted COC for pressure test without any report for diassamble or change parts more over the name plates for Choke manifold valves not changed and several vavles missed its name plate. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API RP 570, API16A | Open | FCS-3 | DRLG
ST-5 | 4.8.17 | Main Plug panel | The DC power supply of all the DC motors bus bars are not protected against electric shock, at plug station inside and outside. | Critical | IADC HSE guide line/API RP 14FZ Ref. 70E | Open | FCS-2 | DRLG
ST-5 | 4.9.27 | Emergency Generator | Engine Diesel Pump is leaking on Engine Starter power connection , high risk of fire during starting the engine in case of loose connection, need to clean accumelated diesel and cover the starter connection with rubber cap to be protected | Critical | IADC HSE Guide lines ,OEM/PMS | Open | FCS-3 | DRLG
ST-5 | 4.11.92 | Welding Machine | Welding electrode holder is in very bad condition , no insulation on holder hand very high risk for electric shock also grounding clamp is missing .Need to replace both holders with new one | Critical | IADC HSE guide line section 6.0.G, OEM/PMS | Open | FCS-3 | DRLG
ST-5 | 4.11.101 | Main camp Engine #1,2 | Engine Diesel Pump is leaking for Engine #1,2 on Engine Starter power connection , high risk of fire during starting the engine in case of loose connection, need to clean accumelated diesel and cover the starter connection with rubber cap to be protected | Critical | IADC HSE Guide lines ,OEM/PMS | Open | FCS-3 | DRLG
ST-5 | 5.6.133 | ## | Power hand tool safety device (safety lock)for grinder not exist and Applying tape to keep the power switch on a hand grinder engaged ,grinder should not be modified as per standard and OEM ,require to replace it to avoid incidents. | Critical | IADC HSE Guidelines 3H,OEM | open | FCS-3 | DRLG
ST-5 | 5.7.46 | ## | Observed wire ropes for DS&ODS air winches kinked ,should be remove from service as per standard to avoid incidents. | Critical | API RP 54 9.6.3D | Open | FCS-3 | DRLG
ST-7 | 0.3.9 | Choke Manifold | No COC, CAT III, CAT IV, UT & Hydro test | Critical | OEM, API RP 4G, API STD 635 | In progress | FCS-1 | DRLG
ST-7 | 1.7.40 | Power Tong | There is hydraulic connection is welded in power tong. | Critical | OEM, IADC, API RP 9B, API 9A | open | FCS-1 | DRLG
ST-7 | 1.7.53 | Power Tong | Mechanism for safety door not equipped, in need to install it to prevent hands fingers injuries and fatality for operators. | Critical | IADC, API Spec 8A, 8C & RP 8B | Open | RA-2 | DRLG
ST-7 | 3.1.41 | BOP HPU |  | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | RA-2 | DRLG
ST-7 | 3.3.20 | Choke Manifold | There is 2 master valves were installed on choke manifold were found two bolts is missed more over name plate is missed and manual hand is missed, required to be installed. | Critical | OEM API RP53, API spec 16C, API 16D, API RP16E, API RP 570 | Open | FCS-1 | DRLG
ST-7 | 3.3.21 | Choke Manifold | Pressure gauges which installed for choke manifold was found thread type, required to be flange type. | Critical | OEM API RP53, API spec 16C, API 16D, API RP16E, API RP 570 | Open | FCS-1 | DRLG
ST-7 | 3.3.22 | Choke Manifold | Filling system for choke manifold valves not arranged, and several doc. Which receive not match Ckoke manifold valves, required to be arranged more over Choke manifold expiration date as per submitted certificates 28 Dec.2022. | Critical | OEM API RP53, API spec 16C, API 16D, API RP16E, API RP 571 | Open | FCS-1 | DRLG
ST-7 | 3.4.5 | Gas separator | While simulate endurance test mud pump against choke manifold observed water flowing from MG separator (5" delivery pipe ) because of corrosion lead to open hole in the pipe wish required to replace MG separator ASAP. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | In progress | FCS-1 | DRLG
ST-7 | 4.2.10 | SCR Plug panel | The DC output bus bars for all DC equipment's not protected against electric hazard . | Critical | HSE guide line | In progress | FCS-1 | DRLG
ST-7 | 4.2.30 | SCR |  | Critical | API-RP-14F 12.6, OEM | Open | FCS-1 | DRLG
ST-7 | 4.7.1 | RCD test | Offices and bedroom RCD "Residual current Devise" & ELCB earth leakage circuit test survey to be done and submitted before rig acceptance. | Critical | IADC, IADC HSE GUIDELINES, API RP 75, API RP 52, API Stud 53 | Open | FCS-1 | DRLG
ST-7 | 4.8.1 | RCD test | All the sleeper room RCD "Residual current Devise" & ELCB earth leakage circuit test survey to be done and submitted before rig acceptance(some of ELCB found faulty). | Critical | IADC, IADC HSE GUIDELINES, API RP 75, API RP 52, API Stud 53 | Open | FCS-1 | DRLG
ST-7 | 4.8.76 | Main Camp | There are two outdoor units missing covers of electrical power terminals and may cause electrical shock hazard | Critical | API RP 14FZ 6.11.1, API RP 14F 4/5C2 .11.8 , | Open | FCS-2 | DRLG
ST-7 | 4.9.11 | Interlock | Interlock between TDS link tilt extend and pipe handler rotating function NOT available (Human failure could lead to serious injury) | Critical | API RP 14FZ, IADC HSE Guide line, OEM | Open | FCS-1 | DRLG
ST-7 | 4.10.5 | Diesel Pump | There is an unused gland in start/stop switch of diesel tank located on diesel tank , need to be removed and replaced by blind gland ASAP | Critical | API RP 14FZ , API RP 505 | Open | RA-2 | DRLG
ST-7 | 5.1.14 | ## | No load test certificates submitted for life post padeyes (5000 pound) located on monkey board and crown ,should to be provided | Critical | IADC HSE CH 20.3 | Open | RA-2 | DRLG
ST-7 | 5.2.21 | ## | LEL sensors located on mud system (shale shaker, mud cleaner) not working, should to be worked ASAP | Critical | IADC HSE CH 10.2L3,13.5 | Open | RA-2 | DRLG
ST-7 | 5.5.30 | ## | Improper fixing for escape device from uncertified anchor point padeye (no load test,mpi cert) , also escape device in wrong position so far from monkey board gate . | Critical | API RP 54 6.10 | Open | RA-2 | DRLG
ST-7 | 5.5.33 | ## |  | Critical | API RP 8 B,IADC HSE CH 3.7 | Open | RA-2 | DRLG
ST-7 | 5.9.23 | ## | No scorpion vaccine available at rig clinic, only ampule available and expired from 6/2023 | critical | API RP 54.4.2 | Open | RA-2 | DRLG
DASCO-31 | 2.4.7 | M/P | Mud cross, pulsation dampener and relief line on the same block at the mud pump discharge manifold, if the strainer blocked then the pulsation dampener can no longer work, causing increased vibration in the lines. (relief line not complete lined up). | Critical | OEM, IADC, API Spec 7K, RP 7L, RP 570 & API RP 54 | Open | FCS-1 | PU
DASCO-31 | 3.1.5 | BOP HPU | Need to check and charge all accumulators bottles, they have low pre-charge pressure less than 1000 psi | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | PU
DASCO-31 | 4.3.4 | BCS | No BCS (Block control system ) / Anti-collusion system for floor saver and crown saver , need to be installed to protect the block from hitting the floor or crown during lowering and hoisting operation | critical | IADC HSE Guide Line | Open | FCS-1 | PU
DASCO-31 | 4.8.2 | E-Light | No E-Lights installed on the following locations (accumulator unit , Mast , Monkey board , Engine room , MCC room , MP area , exit stairs on rig floor , exit stairs on mud system , cellar area , driller cabin area ) | critical | IADC HSE Guide line- API RP 62 2.2.b-API RP 14FZ9.4.4.1 | Open | FCS-1 | PU
DASCO-31 | 5.2.1 | # | There is no fixed gas detection system, that need to be provided and installed | Critical | API RP49 API RP68 | open | FCS-1 | PU
DASCO-31 | 5.2.2 | # | There is no Kitchen wet chemical system available, need to be provided and installed before acceptance | Critical | API RP 54, NFPA 72 | open | FCS-1 | PU
DASCO-31 | 5.2.4 | # | Diesel Fire Pump not connected to be in working order because it missing some items also Fire stations and Fire Fighting hoses not provided, required to be in working order before spud | Critical | API RP 14G API RP54 7.2.2 IADC HSE Reference Guide NFPA 20 | open | FCS-1 | PU
DASCO-31 | 5.2.5 | # | There is (ONLY ONE 30 minutes SCBA + Two 15 minutes SCBA Where one of them empty and the other one below 180 bar) available on rig location, adequate fully charged number of (15 min) and (30 min) Breathing Apparatus should be provided before spud time to can be used while emergency. | critical | API RP49 6.6.1 API RP68 6.5 | open | FCS-1 | PU
DASCO-31 | 5.2.10 | # | Derrickman's escape device (Geronimo) should be Installed during rig up and should be operable when the mast is raised | Critical | IADC HSE Reference Guide 3.15 (B) | in progress | FCS-1 | PU
DASCO-31 | 5.2.11 | # | The rig has no an alarm system. The alarm system should use a distinctive signal for each type of emergency. | Critical | IADC HSE Reference Guide 15.1 (G) | in progress | FCS-1 | PU
DASCO-31 | 5.7.10 | # | While survey and inspection the mobile crane observed that: the back-left side tire in poor condition where it shown a circle crack whole the tire and deep in some areas which has HIPO to be explosive any time results different hazards.so, need to be replaced ASAP | Critical | BS ISO 5057, BS EN1726-1 & BS EN 1726-2 | open | FCS-1 | PU
HT-101 | 1.3.2 | Man rider | Man rider on rig floor fixation direct on rig floor plate, required to be fixed as per OEM recommendation. (Critical) | Critical | IADC, API Spec 8A, 8C & RP 8B | In progress | FCS-1 | WO
HT-101 | 1.3.17 | Power tong | F/T to power tong safety door mechanism malfunction in low gear but working in high gear, it must be operating in all situation. | Critical | IADC, API Spec 8A, 8C & RP 8B | Open | FCS-2 | WO
HT-101 | 2.3.2 | MP 1&2 | Mud pump PRV found thread type recommended to be flange type or union type to avoid excessive force on the thread. especially the upstream side MP-1 & MP-2 are the same. | Critical | API RP 53, API RP 54 | In progress | FCS-1 | WO
HT-101 | 3.2.12 | BOP | BOP P/T not performed due to, BOP stack not lay down on test stump base also there is no test pump provided on location to perform the test. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-2 | WO
HT-101 | 3.3.1 | Choke Manifold | Choke manifold valves missed name plate. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-1 | WO
HT-101 | 3.3.12 | Choke remote panel | While performing F/T to choke remote panel (Swaco) it failed and hydrulic pump malfunction. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API RP 570, API16A | Open | FCS-2 | WO
HT-101 | 4.2.12 | Mast | ACS (Anti Collision System) is Not available (crown-floor saver) | Critical | IADC HSE Guide line | open | FCS-1 | WO
HT-101 | 4.3.10 | Air Compressor | Air Compressor is not EX. Proof Type (Motors and Electrical panel enclosure) and it is located near to hazardous area (cellar area) in addition of that it has the following defects: 1- The electrical panel has a lot of opening holes from inside, 2- Panel also has a lot of opening spaces from the panel cooling fan cover. 3- Main Compressor motor cable gland is missing. 4- The electrical panel has many splices. HIPO for fire accident can happen easily if water or flammable gases or liquids reaches to the electrical connection. All these defects don’t maintain any kind of protection from water or dust and the most important protection which is EX. protection. Corrective action needs to be taken ASAP to fix all defects, compressor location needs to be changed to be in unclassified location (near to engine room) otherwise compressor to be replaced. | Critical | API RP 14FZ 12.3.7 API RP 14FZ 16.3.5 IEC-60079 OEM/PMS | Open | FCS-2 | WO
HT-101 | 4.5.25 | Diesel Tank | Gland of Diesel tank pump Ac motor not EX Type , Cable not fitted properly into gland and Cable covered with diesel .Diesel Pump Ac motor did not have any evidence that is Explosion Proof (missing name plate). | Critical | API RP 505 8.2.1.3.1 , NFPA 30 ,IEC 60079-10 | Open | RA-1 | WO
HT-101 | 4.9.5 | Emergency light | Not available on Mud Tanks, Rig floor, Mast, Swaco control panel, chock manifold | Critical | API RP 540 5.4.1/RP14FZ API RP 14F/RP500-505 IADC HSE Guide line IEC-60079 OEM | Open | FCS-1 | WO
HT-101 | 4.10.11 | Bed Lights | some of bed lights are not in place & wires are not insulated properly (direct power) / and most of it are not function or damaged , also some bed lights switches not connected or installed properly , need to review all rooms bed lights and repair all defects | Critical | IADC HSE Guide line / API RP 54 / OEM | Open | FCS-1 | WO
HT-101 | 4.10.40 | Maintenance crew caravan | Found local hot plate used inside Maintenance crew caravan, it has the following defects: 1- Power cable of the hot plate is spliced 2- Hot plate connected directly without protection Thermostate 3- Hot plate is in bad condition. 4- Using not approved and Defected multi socket cord to supply it. All these defects can lead to electrocution and short circuit lead to fire, Hot plate and local multi socket to removed Immediately. (Also Hot plates are prohibited to be used inside any caravan) | Critical | IADC HSE Guide Lines , API 14F , API 14FZ , OEM/PMS | Open | FCS-2 | WO
HT-101 | 4.11.13 | Electrician Tools | Avometer that available in rig is in very bad condition and may cause electrical shock to electrician while troubleshooting in high voltage circuits | Critical | OEM | Open | RA-1 | WO
HT-101 | 5.2.7 | 0 | There are two sets of Breathing Apparatus equipment in rig floor dog house one of them found empty and the other only half full that not satisfy while emergency, need to be refilling | critical | API RP 68 APIRP 49 | open | FCS-2 | WO
HT-101 | 5.6.35 | 0 | Observed manriding without -low descending device -Emergency stop -limit switch | critical | API RP 54 | open | FCS-1 | WO
HT-101 | 5.6.65 | 0 | There is no life saving post used for installing fall arrest system at monkey board , which should be provided ASAP | Critical | OSHA 1926.502 (b)(i) & OSHA 1910.140 | open | RA-1 | WO
HT-101 | 5.6.74 | 0 | Derrick ladder arrestor is stuck and derrick man tied it on guardrail then forced to go down without any securing against personnel fall, the fall arrestor should get out of service and two arrestor systems should be provided: one for derrick ladder (posted on crow area) and another posted on monkey board each for its specific purpose ASAP | critical | RP54 5.5.1 1910.132(c) OSHA 1926.502 (b)(i) & OSHA 1910.140 | open | RA-1 | WO
HT-101 | 5.6.106 | 0 | Grinder in welding machine observed that: safety device is modified. (Applying tape to keep the power switch on a hand grinder engaged.)) which lead to HIPO hazards, the modification need to be maintained or replace the grinder with new safety one. | Critical | IADC HSE Guidelines 3.0.H | open | FCS-2 | WO
HT-101 | 5.6.107 | 0 | Flammable liquids and paint gallons observed stored inside wooden cupboard inside maintenance workshop also Freon cylinder kept inside where there is a poor ventilation which means HIPO for fire hazards any time, required to be removed and stored in good ventilated location | Critical | API RP54 7.1.1 API RP54 8.3.12 API RP54 8.4.2 | open | FCS-2 | WO
HT-101 | 5.7.9 | 0 | Rig Floor Air winch (S.N:A024383) regarding all rejection criteria which are: 1- The proof load test which submitted not matched with the standard load test requirements as API RP 8B (8.3), that state:(proof load test performing by applying a load equal 1.5 times the rated load of the equipment) where the rated load of the winch present here is 5 tons and the proof test certificate is only 3.75 ton. 2- The spring-back throttle device that returns to neutral when it is released found malfunction. 3- Only one break system is used which working but improperly. 4- The winch not equipped with an-emergency shut off valve 5- The winch not equipped with spooling mechanism that ensures the line is properly wound on the drum. 6- Nails and nuts used to fix the winch base that may lose any time The recommendation: this winch should be replaced with standard one to provide safely lifting work | critical | API RP 8B IADC HSE Guideline 19.6 | open | FCS-2 | WO
HT-101 | 5.7.11 | 0 | (ODS) HYD/WINCH on carrier observed there are no wraps of wire left on the winch drum while the lowering operation which means the hoist wires not long enough, need to be replaced with another certified wire ASAP | critical | OEM IADC HSE Guideline | open | FCS-2 | WO
HT-101 | 5.10.18 | 0 | No fixed emergency fire fighting wet chemical system at kitchen,should be installed | critical | API RP 54 | open | FCS-1 | WO
ECDC-9 | 2.4.18 | MP | During test mud pump PRV the gauge failure in 3800psi mud pump pressure gauge thread type, in need to change to flange type for mud pump and stand pipe. | Critical | IADC, API RP 53 | Open | RA-1 | WO
ECDC-9 | 3.3.6 | Choke Manifold | pressure gauge thread type, in need to change to flange type | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API RP 570, API 16A | Open | RA-1 | WO
ECDC-9 | 5.2.3 | ## | There is no fixed gas system (H2S AND LEL) at rig location that need to be provided. | critical | API RP RP49 API RP68 API RP 62 3.2.5 | Open | FCS-1 | WO
ECDC-9 | 5.6.57 | ## |  | Critical | OEM | open | RA-1 | WO
ECDC-9 | 5.7.17 | ## | Multiple of safety fetures at man riding malfunction such as. - Slack wire detector. - Two independent auto brakes: an internal multidisc brake and external drum band brake. - Overload limit switch. - Emergency lowering system. - Button release the emergency shut down button stuck. | Critical | OEM | open | FCS-1 | WO
ECDC-9 | 5.7.18 | ## | Found front right tire for forklift worn-out (in bad condition) with deep holes, should to be replaced immediately. | Critical | IADC HSE CH.9 O | open | RA-1 | WO
EDC-40 | 4.8.1 | Diesel Tank | Fuel Purifier AC motor is not Explosion Proof type need to be replaced by EX type motor. | Critical | API RP 500 8.2.1.4 , API RP 14FZ , IADC HSE Guide Lines , IEC 60079 | Open | FCS-1 | DRLG
EDC-40 | 4.11.4 | Grounding | Ground reading in fly camp , TD VFD unit , SCR and Main Camp are high (between 5.7 and 15 OHM) . (Ideally a ground should be of zero ohms resistance, that is recognized by all agencies, however the IEEE and NFPA have recommended a ground resistance value of 5 ohms or less). | Critical | IADC HSE Guid line API RP 54, IEEE std 142, NEC table 250-66, NFPA 70 , API RP 540 | Open | FCS-1 | DRLG
EDC-40 | 5.2.6 | 0 | There is no 30 minute SCBA (Self Contained Breathing Apparatus) available on rig location, should be provided before spud time. | critical | API RP49 6.6.1 API RP68 6.5 | open | FCS-1 | DRLG
EDC-40 | 5.2.9 | 0 | Derrick man's escape device (Geronimo) should be Installed during rig up and should be operable when the mast is raised | Critical | IADC HSE Reference Guide 3.15 (B) | open | FCS-1 | DRLG
EDC-40 | 5.7.4 | 0 | The lines of man riding observed come in contact with the CSB that should be considered before spud. | Critical | API RP54 9.6.7 | open | FCS-1 | DRLG
EDC-40 | 5.7.5 | 0 | The lines of (OSD) observed come in contact with the monkey board fingers that should be considered before spud. | Critical | API RP54 9.6.7 | open | FCS-1 | DRLG
EDC-40 | 5.7.6 | 0 | CSG Stabbing Board not in working order where it is still missing its essential items that should be available and provided, which are: - COC not mention its SWL - its hoist load test certificate - Fall protection system - Safety lines that should be attached - Both locking devices their functions not tested/checked yet. | Critical | IADC HSE Guideline 3.25 | open | FCS-1 | DRLG
EDC-40 | 5.7.7 | 0 | During F/T for Mobile Crane Limit switch, it observed not working properly may lead to hazards. | Critical | IADC HSE Guideline 8.1 | open | FCS-1 | DRLG
EDC-40 | 5.8.1 | 0 | Diesel Fire Pump isn’t in working order, which required to be ready and in working order ASAP. | critical | API RP54 7.2.2 IADC HSE Reference Guide NFPA 20 | open | FCS-1 | DRLG
EDC-40 | 5.11.2 | 0 | There is only one ampule of Snake vaccine in rig clinic, the other types of vaccines for scorpion also for snake and anti- tetanus ampules require to be provided. | critical | EDC Onshore Contingency Manual,WHO, API RP 54, IADC HSE Guidelines | open | FCS-1 | DRLG
EDC-40 | 5.11.3 | 0 | There is no oxygen cylinder in clinic used for emergency that need to be provided | critical | EDC Onshore Contingency Manual,WHO, API RP 54, IADC HSE Guidelines | open | FCS-1 | DRLG
EDC-12 | 1.6.5 | Power Tong | F/T Power Tong safety gate latch, not activated when it operated need be fixed ASAP | Critical | IADC, API Spec 8A, 8C & RP 8B | open | RA-3 | WO
EDC-12 | 5.9.82 | Kitchen Ventilation | Kitchen ventilation hood shows excessive grease from inside duct, require to perform schedule for deep clean to avoid fire hazard | Critical | API RP 54, NFPA 30, OSHA 1910.106 | open | RA-3 | WO
EDC-76 | 5.7.9 | 0 | Load test for the fall arrestor pad eyes located above the monkey board performed on (1000 kilos) but according to IADC standards should be performed the load test at least on (2268 kilos) | critical | IADC HSE CH 20.3 C | open | FCS-1 | DRLG
EDC-76 | 5.7.14 | 0 | There is a Malfunction in distance limit switch device at mobile crane (S:N BR1040), should to be repaired or changed ASAP. | critical | IADC HSE CH 8.1G | open | FCS-1 | DRLG
EDC-76 | 5.11.1 | 0 | No AED (Automated External Defibrillator) device for CPR at rig clinic, should to be provided for emergency case | critical | API RP 4.2.1, 4.3.1 | open | FCS-1 | DRLG
EDC-75 | 5.10.82 | ## | Found discharge line for fixed fire protection system ( wet chemical system for kitchen ) broken and smached, require 3rd party co. to replace it ASAP | Critical | API RP 14G,NFPA 11,15 | Open | RA-2 | DRLG
EDC-9 | 5.10.23 | ### | Kitchen air curtain allocated above entrance door shows excessive grease which require cleaning or replacing to prevent a serious fire hazard. | Critical | API RP 54 7.1, NFPA 30 | open | RA-1 | DRLG
EDC-9 | 5.11.8 | ## | Pads used with VED (automated external defibrillator) only one set provided which connected to the device and also it expired on june 2023, new pad sets need to be provided soon. | Critical | WHO, IADC HSE Guidelines EDC HSE manual | open | FCS-2 | DRLG
NDC-4 | 1.2.4 | DW | There is CAT III submitted for DW brake, which require to be performed every 6 monthes | Critical | OEM, IADC | Open | RA-1 | WO
NDC-4 | 2.6.15 | Main camp eng.no.2 | There is diesel leakage at main camp eng. No.2 and there is diesel bucket under leaking part. | Critical | OEM, IADC HSE guidelines Ch.5 | Open | RA-1 | WO
NDC-4 | 3.3.15 | Choke Manifold | Chock manifold completely changed by another 10K choke manifold, there is no certificate submitted only pressure test certificate submitted as COC without mention any mentions for work done such Disassemble, spare parts used, Non Distractive test more over several valves missed name plate. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | RA-1 | WO
NDC-4 | 4.2.17 | Grounding | Main Grounding cable connected to well head in cellar area is missing , need to be connected ASAP. | Critical | API RP 14FZ Section 6.10.3 API RP 540 section 5.4 , NEC 250.66 , IEC-60079 | Open | RA-1 | WO
NDC-4 | 4.10.29 | Diesel Welding machine | Diesel Welding machine is in very bad condition and it is unsafe to be used as it has the following : 1- Electrical bridge side cover not installed properly and it doesn’t maintain the integrity of protection against water and dust , HIPO for short circuit or electrocution. 2- (-Ve) wire clamp wiring is very poor and loosely connected . 3- Electrode holder in very bad condition , HIPO for electrocution during welding job , need to be replaced by new one. 4- power cable spliced using electrical table and connected to C.B outside without any kind of protection , HIPO for shirt circuit and electrocution. 5- no cover installed for Engine driving Belt for engine cooling fan, need to be installed . Diesel welding machine has to be out of service till all defects mentioned above are rectified or to be replaced by new diesel welding machine. | Critical | API RP 14 F , API RP 14 FZ , IADC HSE Guide lines , OEM/PMS | Open | RA-1 | WO
NDC-4 | 4.11.15 | UPS | - CCTV system should be powered through UPS to provide continuous monitoring and recording of all Cameras positions in case of blackout or power loss to help all key persons to take proper decision in case of any emergency case or somebody stuck on monkey board or stabbing board -Fixed Gas detection system and warning alarms of the fixed fire detection/fighting system should be powered through UPS to provide continuous monitoring for GAS level values for H2S/LEL and help in taking proper and fast action in case of gas release - Rig communication and Paging system should be powered through UPS to provide continuous power supply in case of blackout or power loss and provide continuous communication between rig Crew and to announce any emergency or evacuation cases. | Critical | API RP 14F , API RP 14 FZ section 10.5 | Open | FCS-1 | WO
NDC-4 | 4.12.49 | Galley Equipment | No ELCB ( Earth leakage Circuit breaker ) installed for all galley equipment , Each equipment must be power though ELCB 30 mA to protect human against any case of ground fault. | Critical | IADC HSE Guidelines API RP 52, API RP 54, API RP 14FZ 9.4.2 | Open | FCS-1 | WO
NDC-4 | 4.12.52 | Dry Store | ELCB ( Earth leakage circuit breaker) installed inside dry store fail to trip manually , need to be tested using RCD tester and if test fail the ELCB must be replaced immediately | Critical | IADC HSE Guidelines API RP 52, API RP 54, API RP 14FZ 9.4.2 | Open | FCS-1 | WO
NDC-4 | 4.12.53 | Floor man Room | Floor man Room top bed light cover is missing and all electrical wiring are clear , very high risk for electrocution , cover need to be installed immediately or complete bed light to be replaced | Critical | IADC HSE Guide lines , OEM/PMS | Open | FCS-1 | WO
NDC-4 | 4.12.55 | ASS -D caravan | ELCB ( Earth leakage circuit breaker) installed inside Ass-D caravan electrical panel fail to trip manually , need to be tested using RCD tester and if test fail the ELCB must be replaced immediately | Critical | IADC HSE Guidelines API RP 52, API RP 54, API RP 14FZ 9.4.2 | Open | FCS-1 | WO
EDC-86 | 1.1.33 | Carrier | Diesel line between diesel tanks underneath carrier had diesel leakage require to be fixed more over diesel filling hose found ball valve leaking diesel, require to fix diesel leakage. | Critical | IADC HSE Guidelines CH 5 | OPEN | RA-3 | WO
EDC-86 | 3.2.11 | BOP | There is control hose at BOP side found damaged require to be replaced. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | RA-3 | WO
EDC-86 | 4.5.5 | UPS | All the following loads should be power through UPS to provide continuous power supply incase of power loss or black out: 1- Instrumentation DAQ and Driller HMI to provide continuous storage for Data , calibration and monitoring for and drilling parameters . 2- Fixed Gas Detection system and Alarm system to provide continuous monitoring for gas levels and also alarm incase of any emergency gas release cases. 3- Rig communication and paging system to provide continuous communication between crew during emergency case. 4- CCTV system should be powered through UPS to provide continuous monitoring and recording of all Cameras positions in case of blackout or power loss to help all key persons to take proper decision in case of any emergency case or somebody stuck on monkey board or stabbing board. 5- BCS system should be power through UPS to provide continuous supply for the BCS to provide full protection for crown safer and floor saver during any shutdown or black-out for main engine due to any emergency cases | Critical | API RP 14F , API RP 14 FZ section 10.5 | Open | RA-3 | WO
EDC-86 | 5.7.16 | # | Improper anchoring for the fall arrestor at the crown section due to it anchored at the handrail of crown which is should provide the mast with separated pad eye or equivalent for anchorage point and must be capable of supporting at least 5000 pounds (2268 kilos)per employee also FYI most standard guardrail systems are not adequate anchorage points because they are not built to withstand the Impact forces generated by a fall. | critical | IADC HSE Guidelines 20.3 C | open | RA-3 | WO
EDC-85 | 5.7.16 | Fall arrestor | Fall arrest system not implemented on monkey board and should be provided ASAP because fall arrest system used to arrest an employee in a fall from a working level. It consists of an anchorage,connectors, a body belt or body harness and may include a lanyard, deceleration device, life line | critical | OSHA 1926.502 | open | FCS-2 | WO
EDC-85 | 5.9.42 | Main Camp | Kitchen ventilation hood shows oil leakage and shows excessive grease from outside that presenting a serious fire hazard which require an immediate cleaning and to be directed for a monthly cleaning schedule. | Critical | API RP 54 7.1, NFPA 30 | Open | FCS-1 | WO
EDC-85 | 5.6.72 | # | Rig floor support legs unleveled properly where they positioned over wood pieces and a part of the leg's base suspended in air that may cause rig floor falling if there is abnormal load or tension sudden happen, this point need to be highly considered | critical | API RP54 9.2.6 | Open | FCS-3 | WO
EDC-85 | 5.6.75 | # | A box of paint gallons located in rig location and directly supposed to sunshine (may be heated) that may lead to fire hazard any time, need to be kept inside good ventilated store or removed out of location | critical | API RP54 8.4.2 | Open | FCS-3 | WO
EDC-85 | 5.7.19 | Forklift | Left back side fork's tire observed in very poor condition it observed totally smooth, required to replaced immediately to avoid different hazards | Critical | EDC SAFETY MANUAL, OSHA 1910.109(d)(2)(iv)(f) , ASME B56.6–1992 | In progress | FCS-3 | WO
EDC-85 | 3.1.18 | BOP HPU | Electrical triplex pump, fluid end oil seals were damaged and there is hydraulic oil leaking in the triplex pump pan. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | open | FCS-3 | WO
EDC-85 | 5.11.3 | Rig Clinic | Pads used with VED (automated external defibrillator) only one set provided which connected to the device and also it expired on oct. 2022, new pad sets need to be provided soon. | Critical | WHO, IADC HSE Guidelines EDC HSE manual | open | FCS-3 | WO
EDC-85 | 5.9.113 | Main Camp | Two lugs of water tank colored with red color and rejected from the lifting 3rd party company and still no action taken which may causing dropped object hazard while lifting the tank. Need to be repaired deeply or removed from the service ASAP | Critical | ASTM E709:2015 | Open | FCS-3 | WO
EDC-53 | 4.1.18 | MP 2 DCM B | MP2 DCM#B side inspection cover is missing , high risk for short circuit of fire to Motor winding in case water enter to the motor , also it doesn’t maintain any kind of EX. Protection , cover need to be installed immediately | Critical | API RP 14FZ 12.3.7 API RP 14FZ 16.3.5 IEC-60079 OEM | Open | RA-3 | DRLG
EDC-53 | 5.7.31 | Liftng | During the deep inspection on survival equipment tripod wench found some of rejection items such as OEM name plate of structure missing and the galvanized wire sling contained several kinks, twist and lose wire flexibility( wire rope S.N:E004010025E5D4A6) which is require providing the rig with tripod in good condition and certified. | Critical | ANSI Z359.1, ANSI Z359.4, ANSI Z117.1, BS EN 13414 OEM | Open | RA-3 | DRLG
EDC-53 | 5.7.46 | # | Pad eye of life post placed on monkey board without any of MPI & load test inspection which is should be tested for anchorage point and must be capable of supporting at least 5000 pounds (2268 kilos)per employee. | Critical | IADC HSE Guidelines 20.3 C | Open | RA-3 | DRLG
EDC-53 | 3.4.15 | Choke Manifold |  | Critical | API RP 53 17.10.3 API RP 53 section 8.2 | Open | RA-3 | DRLG
EDC-91 | 5.9.22 | Rig Camp | Cook Hot plate observed located into Rig Camp's cabin which presents different hazards (i.e.: fire hazard, burn hazard,…) that is prohibited to be used inside cabins | Critical | API RP 54, API RP 14F,14FZ OEM/PMS IADC HSE Guidelines | Open | RA-3 | WO
EDC-91 | 5.11.44 | Mast | Mast lighting not adequate may lead to personnel falling or hard injuries (especially the upper section and in front the monkey board) which need to be improved | Critical | API RP54 9.14.7 | Open | FCS-1 | WO

## phases (hidden)
PHASES
All
FCS-1
RA-1
FCS-2
RA-2
FCS-3
RA-3

## Phase_Dates
Rig_No. | Phase | Date
EDC-91 | FCS-1 | 2021-02-09
EDC-90 | FCS-1 | 2021-03-17
EDC-58 | FCS-1 | 2021-03-19
EDC-62 | FCS-1 | 2021-04-21
EDC-12 | FCS-1 | 2021-04-23
EDC-57 | FCS-1 | 2021-04-29
EDC-97 | FCS-1 | 2021-05-15
EDC-54 | FCS-1 | 2021-05-20
EDC-93 | FCS-1 | 2021-05-22
EDC-87 | FCS-1 | 2021-05-29
EDC-17 | FCS-1 | 2021-05-31
EDC-95 | FCS-1 | 2021-05-31
EDC-88 | FCS-1 | 2021-06-01
EDC-61 | FCS-1 | 2021-06-23
EDC-53 | FCS-1 | 2021-07-01
EDC-32 | FCS-1 | 2021-07-02
EDC-89 | FCS-1 | 2021-07-12
EDC-86 | FCS-1 | 2021-07-15
ST-5 | FCS-1 | 2021-08-18
EDC-84 | FCS-1 | 2021-09-16
EDC-83 | RA-1 | 2021-09-22
EDC-42 | FCS-1 | 2021-10-14
EDC-50 | FCS-1 | 2021-10-14
EDC-92 | FCS-1 | 2021-11-04
EDC-48 | FCS-1 | 2021-11-09
EDC-97 | RA-1 | 2021-12-14
EDC-54 | RA-1 | 2021-12-16
EDC-17 | RA-1 | 2021-12-17
EDC-61 | RA-1 | 2021-12-18
EDC-57 | RA-1 | 2021-12-20
EDC-58 | RA-1 | 2021-12-22
EDC-95 | RA-1 | 2021-12-24
EDC-91 | RA-1 | 2021-12-26
EDC-88 | RA-1 | 2021-12-28
EDC-89 | RA-1 | 2022-01-19
EDC-53 | RA-1 | 2022-01-20
EDC-86 | RA-1 | 2022-01-22
EDC-87 | RA-1 | 2022-01-25
EDC-90 | RA-1 | 2022-01-28
EDC-62 | RA-1 | 2022-01-28
EDC-32 | RA-1 | 2022-01-30
EDC-93 | RA-1 | 2022-01-31
EDC-91 | FCS-2 | 2022-02-20
EDC-90 | FCS-2 | 2022-02-21
EDC-1 | FCS-1 | 2022-02-23
EDC-48 | RA-1 | 2022-03-02
EDC-86 | FCS-2 | 2022-03-19
EDC-83 | RA-2 | 2022-03-20
EDC-58 | FCS-2 | 2022-04-01
EDC-42 | RA-1 | 2022-04-15
EDC-12 | RA-1 | 2022-04-18
EDC-57 | RA-2 | 2022-04-21
EDC-61 | FCS-2 | 2022-04-22
EDC-57 | FCS-2 | 2022-04-27
EDC-54 | FCS-2 | 2022-04-29
EDC-95 | FCS-2 | 2022-05-16
EDC-82 | FCS-1 | 2022-05-18
EDC-50 | RA-1 | 2022-05-25
ST-7 | FCS-1 | 2022-05-27
EDC-11 | FCS-1 | 2022-05-31
HT-101 | FCS-1 | 2022-06-14
EDC-17 | FCS-2 | 2022-06-15
ST-5 | RA-1 | 2022-06-24
EDC-87 | FCS-2 | 2022-06-25
EDC-75 | FCS-1 | 2022-07-10
EDC-53 | FCS-2 | 2022-08-13
EDC-48 | FCS-2 | 2022-08-13
EDC-1 | RA-1 | 2022-08-18
EDC-97 | FCS-2 | 2022-09-07
EDC-42 | FCS-2 | 2022-09-12
ST-5 | FCS-2 | 2022-09-13
EDC-84 | RA-1 | 2022-09-14
EDC-92 | RA-1 | 2022-09-17
EDC-93 | FCS-2 | 2022-09-22
EDC-32 | FCS-2 | 2022-09-22
EDC-88 | FCS-2 | 2022-09-24
EDC-91 | RA-2 | 2022-10-11
EDC-89 | FCS-2 | 2022-10-13
EDC-89 | RA-2 | 2022-10-13
EDC-12 | FCS-2 | 2022-10-17
EDC-61 | RA-2 | 2022-10-17
EDC-11 | RA-1 | 2022-10-18
EDC-62 | RA-2 | 2022-10-22
EDC-54 | RA-2 | 2022-10-22
EDC-62 | FCS-2 | 2022-10-22
EDC-92 | FCS-2 | 2022-11-12
EDC-97 | RA-2 | 2022-11-13
EDC-17 | RA-2 | 2022-11-13
EDC-90 | RA-2 | 2022-11-15
EDC-82 | RA-1 | 2022-11-16
EDC-50 | FCS-2 | 2022-11-17
EDC-53 | RA-2 | 2022-11-25
EDC-9 | FCS-1 | 2022-11-29
ST-5 | RA-2 | 2022-12-18
EDC-48 | RA-2 | 2022-12-22
ST-7 | RA-1 | 2022-12-23
EDC-53 | RA-2 | 2022-12-24
EDC-1 | FCS-2 | 2023-01-11
EDC-86 | RA-2 | 2023-01-11
EDC-58 | FCS-3 | 2023-01-14
EDC-42 | RA-2 | 2023-01-17
EDC-95 | RA-2 | 2023-01-17
EDC-57 | FCS-3 | 2023-01-20
EDC-9 | RA-1 | 2023-01-23
ECDC-9 | FCS-1 | 2023-01-24
EDC-75 | RA-1 | 2023-01-27
EDC-49 | RA-1 | 2023-02-01
EDC-17 | FCS-3 | 2023-02-09
EDC-89 | FCS-3 | 2023-02-09
EDC-54 | FCS-3 | 2023-02-12
EDC-61 | FCS-3 | 2023-02-14
EDC-62 | FCS-3 | 2023-02-19
EDC-84 | FCS-2 | 2023-02-20
ST-7 | FCS-2 | 2023-02-21
EDC-90 | FCS-3 | 2023-02-21
NDC-4 | FCS-1 | 2023-03-07
ST-5 | FCS-3 | 2023-03-09
EDC-50 | RA-2 | 2023-03-09
EDC-31 | FCS-3 | 2023-03-10
EDC-92 | FCS-3 | 2023-03-12
EDC-48 | FCS-3 | 2023-03-14
EDC-87 | RA-2 | 2023-03-15
EDC-12 | FCS-3 | 2023-03-16
HT-101 | RA-1 | 2023-03-17
EDC-82 | FCS-2 | 2023-03-19
EDC-91 | FCS-3 | 2023-03-20
EDC-75 | FCS-2 | 2023-04-05
EDC-93 | RA-2 | 2023-04-05
EDC-9 | FCS-2 | 2023-04-08
EDC-83 | FCS-3 | 2023-04-13
EDC-95 | FCS-3 | 2023-04-24
EDC-49 | FCS-2 | 2023-04-27
EDC-86 | FCS-3 | 2023-04-30
EDC-11 | FCS-2 | 2023-05-02
EDC-53 | FCS-3 | 2023-05-16
EDC-87 | FCS-3 | 2023-05-21
EDC-84 | FCS-3 | 2023-05-22
EDC-88 | FCS-3 | 2023-05-26
EDC-50 | FCS-3 | 2023-06-03
EDC-58 | RA-3 | 2023-06-08
HT-101 | FCS-2 | 2023-06-10
SDF-01 | FCS-1 | 2023-06-13
EDC-97 | FCS-3 | 2023-06-14
EDC-93 | FCS-3 | 2023-06-16
DASCO-31 | FCS-1 | 2023-06-18
EDC-1 | RA-2 | 2023-07-05
EDC-65 | FCS-1 | 2023-07-06
EDC-54 | RA-3 | 2023-07-06
ST-7 | RA-2 | 2023-07-10
EDC-61 | RA-3 | 2023-07-11
EDC-89 | RA-3 | 2023-07-15
EDC-90 | RA-3 | 2023-07-16
ECDC-9 | RA-1 | 2023-07-19
EDC-17 | RA-3 | 2023-08-01
EDC-49 | FCS-1 | 2023-08-01
EDC-42 | FCS-3 | 2023-08-06
EDC-57 | RA-3 | 2023-08-06
EDC-62 | RA-3 | 2023-08-12
EDC-40 | FCS-1 | 2023-08-13
EDC-92 | RA-3 | 2023-08-13
EDC-12 | RA-3 | 2023-08-20
EDC-76 | FCS-1 | 2023-09-01
EDC-49 | RA-2 | 2023-09-08
EDC-75 | RA-2 | 2023-09-08
EDC-9 | RA-2 | 2023-09-09
NDC-4 | RA-1 | 2023-09-13
EDC-86 | RA-3 | 2023-09-16
EDC-85 | FCS-3 | 2023-09-23
EDC-53 | RA-3 | 2023-09-29
DASCO-31 | FCS-1 | 2023-10-07
EDC-91 | RA-3 | 2023-10-09
EDC-88 | RA-3 | 2023-10-12
EDC-95 | RA-3 | 2023-10-13
EDC-31 | RA-3 | 2023-10-15
EDC-11 | RA-2 | 2023-10-16
EDC-93 | RA-3 | 2023-10-26
EDC-87 | RA-3 | 2023-10-29
EDC-48 | RA-3 | 2023-11-06
EDC-50 | RA-3 | 2023-11-11
EDC-84 | RA-3 | 2023-11-22
EDC-97 | RA-3 | 2023-11-26

## Plan
Team_No. | Audit/Drops | Rig_Order | Rig_No. | Job Type | Expected Date | Expected Stay On
Team_1 | Audit | 1 | Home | No Job
Team_1 | Audit | 2 | Home | No Job
Team_1 | Audit | 3 | Home | No Job
Team_2 | Audit | 1 | Home | No Job
Team_2 | Audit | 2 | Home | No Job
Team_2 | Audit | 3 | Home | No Job
Team_3 | Audit | 1 | EDC-32 | RA-3 | 2023-12-13 | 2
Team_3 | Audit | 2 | EDC-83 | RA-3 | 2023-12-16 | 3
Team_3 | Audit | 3 | Home | No Job
Team_1 | Drops | 1 | EDC-54 | 4th | 2023-11-07 | 3
Team_1 | Drops | 2 | EDC-88 | 4th | 2023-11-10 | 2
Team_1 | Drops | 3 | EDC-12 | 4th | 2023-11-12 | 2
Team_1 | Drops | 4 | EDC-9 | 5th | 2023-11-22 | 3
Team_1 | Drops | 5 | EDC-11 | 5th | 2023-11-25 | 3
Team_1 | Drops | 6 | EDC-62 | 5th | 2023-11-28 | 3
Team_2 | Drops | 1 | EDC-49 | 4th | 2023-11-06 | 3
Team_2 | Drops | 2 | EDC-57 | 4th | 2023-11-09 | 3
Team_2 | Drops | 3 | EDC-87 | 5th | 2023-11-12 | 2
Team_2 | Drops | 4 | EDC-91 | 5th | 2023-11-14 | 2
Team_2 | Drops | 5 | EDC-93 | 5th | 2023-11-16 | 2
Team_2 | Drops | 6 | EDC-48 | 5th | 2023-11-28 | 3
Team_3 | Drops | 1 | EDC-1 | 5th | 2023-11-15 | 3
Team_3 | Drops | 2 | EDC-89 | 5th | 2023-11-18 | 2
Team_3 | Drops | 3 | EDC-85 | 5th | 2023-11-20 | 3
Team_3 | Drops | 4 | EDC-58 | 3rd | 2023-11-22 | 3
Team_3 | Drops | 5 | EDC-83 | 5th | 2023-11-25 | 2

## Team_Management
Team_No. | Audit/Drops | Rig_Order | Rig_No. | Job Type | Actual Date
Team_1 | Audit | -1 | EDC-95 | RA-3 | 2023-10-13
Team_1 | Audit | 0 | Home | No Job | 2023-10-17
Team_1 | Audit | 1 | Home | No Job | 2023-10-24
Team_2 | Audit | -1 | EDC-84 | RA-3 | 2023-11-22
Team_2 | Audit | 0 | EDC-97 | RA-3 | 2023-11-26
Team_2 | Audit | 1 | Home | No Job | 2023-11-29
Team_3 | Audit | -1 | EDC-48 | RA-3 | 2023-11-06
Team_3 | Audit | 0 | EDC-50 | RA-3 | 2023-11-11
Team_3 | Audit | 1 | Home | No Job | 2023-11-16
Team_1 | Drops | -1 | EDC-62 | 5th | 2023-11-10
Team_1 | Drops | 0 | EDC-48 | 5th | 2023-12-01
Team_1 | Drops | 1 | EDC-57 | 4th | 2023-12-04
Team_2 | Drops | 0 | EDC-9 | 5th | 2023-11-11
Team_2 | Drops | 0 | Home | No Job | 2023-11-14
Team_2 | Drops | 1 | EDC-87 | 5th | 2023-11-11
Team_3 | Drops | -1 | EDC-58 | 3rd | 2023-11-19
Team_3 | Drops | 0 | EDC-91 | 5th | 2023-11-22
Team_3 | Drops | 1 | EDC-87 | 5th | 2023-11-24

## Rig_Mast_Problems_Drops
Rig_No. | Mast Problem Description | Rig_Type
EDC-17 | The Mast fall prevention system was in poor condition, as the climb assist was stuck and the secondary retention of the fall arrestor secured at the same anchor point. | DRLG
EDC-90 | the fall arrestor that was mentioned as a critical item, fall arrestor installed on the handrail and No load testthere is no SR pad-eye. | WO
EDC-97 | A complete cut was observed in one of the mast ladder steps above 10 steps from the monkey board, it is recommended to avoid any claiming at the mast till fixing this problem | WO
EDC-31 | The Mast fall arrestor is secured with a not standard pad-eye, as it is welded to the crown block handrail. Besides it has no load test, and the secondary retention wire of the fall arrestor secured to the handrail is without a pad-ey | PU
EDC-84 | the fall arrestor that was mentioned as a critical item, fall arrestor installed on the handrail and No load testthere is no SR pad-eye. | WO
HT-101 | fall arrestor is stuck | WO
ECDC-9 | 1. Climb assist doesn't have prevention system or even there is no separate fall arrestor. 2. Carabiner has a lot of kinks and completely loose "Not Tensioned at all". 3. The bottom anchor point at ladder base is locally made "Not Standard" | WO
NDC-4 | fall arrestor pad eyes has no load test | WO
EDC-50 | Fall Protection System: The fall protection system used does not match the standard personnel securing requirements, where: fall arrestor device is anchored on the derrick ladder used for climbing the first section of the derrick ladder then the derrick man takes off this system and uses the carbineer system from the 2nd section while standing on the derrick ladder which may lead to personnel falling hazard. The fall protection system should reach the Fall Arrestor : There is no fall arrestor at the crown block. , Fall Protection Wire : Observed the fall protection wire had a lot of kinks so it will make a barrier for anyone who will use it as a securing method. | DRLG
ST-5 | # The vertical lifeline on the mast ladder has some kinks, so cannot use it due to the stuck of the carabiner. # The climb assistant device wire is not smoothly UP/Down while using it due to the wire size not being compatible with its counterweight and the sheave above the crown. # ( The wire should be 3/8 inch, To achieve the balance between the weight of the wire and the weight of the counterweight Currently the wire is 5/8’’ inch ) # There is no fall arrestor at the crown block. | DRLG
ST-7 | The Mast could not be inspected because the fall prevention system (Vertical lifeline) is in a very bad condition, it is observed that the wire is very rusted, loosen, and has no hard eye. Also, the anchor point is not standardized, as it is secured with a not coded color shackle to a damaged ladder step. | DRLG